## RTUFLYER
Roof Top Unit Systems Test Reports

## RTU-PW01
INTERNAL USE ONLY - DOES NOT PRINT
GENERAL FIELD CALC. AREA
ROOF TOP UNIT TEST REPORT
PROJECT |  |  | EHC - Tallahassee Reno. & Add. | [9 empty] | SYSTEM |  | RTU-PW01
AREA SERVED |  |  | Private Rooms | [9 empty] | LOCATION |  | Roof
UNIT DATA | [12 empty] | FILTER DATA | [9 empty] | MOTOR ACTUAL BHP CALCS.
MFG. |  |  |  | Aaon | [8 empty] | FILTER SECTION | [10 empty] | AMPS. | VOLTS |  |  |  |  | AMP IMBALANCE TEST1 |  | VOLT IMBALANCE TEST2
TYPE | [12 empty] | QUANTITY | [9 empty] | TEST 1 |  |  | MOTOR EFF.
MODEL NO. | [12 empty] | SIZE (in.) | [9 empty] | TEST 2
SERVICE |  |  |  | Conditioned Air | [8 empty] | TYPE | [9 empty] | TEST 3 |  |  | POWER FACTOR
SERIAL NO. | [12 empty] | S.P. ACROSS |  |  |  | "w.c. |  |  |  | "w.c. |  | AVG. | [6 empty] | 1. Amp imbalance may indicate problems with the motor or power supply.
[13 empty] | CONDITION | [12 empty] | MOTOR PHASE |  |  |  | 2. Volt imbalance may cause motors to overheat. Many solid-state motor controllers and inverters are sensitive to imbalanced voltage.
SUPPLY FAN DATA
|  | CFM |  | TSP |  | ESP |  | RPM |  | BHP |  | ROTATION | [10 empty] | POWER TRANSMISSION (PT) CALCS. | [7 empty] | DETERMINING FAN ROTATION
DESIGN |  | 3825 | [20 empty] | MTR TO FAN SHEAVE RATIO
ACTUAL | [22 empty] | CALC. BELT LENGTH |  |  |  |  | "
FAN MOTOR RPM PER PT
AIRFLOW DATA | [11 empty] | POWER TRANSMISSION DATA |  |  |  |  | X | [5 empty] | MIN. FAN MTR RPM PER PT1
|  |  |  | RETURN |  |  | OUTSIDE |  |  |  |  | TRANSMISSION TYPE | [10 empty] | 1. If fan motor RPM falls below this min. number (cell red) check for belt slippage or belt riding on motor shaft. Based on 0.5" reduction on motor and fan sheave.
DESIGN (CFM) | [6 empty] | 1148 |  |  |  |  | MOTOR SHEAVE MFG.
ACTUAL (CFM) | [11 empty] | MOTOR SHEAVE |  |  |  |  | "I.D. |  |  |  | "O.D.
DAMPER POS. | [5 empty] | Open |  |  | Open |  |  | FAN SHEAVE MFG.
[12 empty] | FAN SHEAVE |  |  |  |  | "I.D. |  |  |  | "O.D.
MOTOR DATA |  |  | X | [8 empty] | BELT MFG.
MFG. | [11 empty] | NO. BELTS & SIZE | [5 empty] | @
FRAME | [11 empty] | CENTER DISTANCE | [6 empty] | "C.C.
H.P. | [22 empty] | DUCT DP SETPOINT CALC. (+20% Tol.)
SERVICE FACTOR | [15 empty] | DUCT STATIC PRESSURE | [6 empty] | #REF!
[5 empty] | DESIGN |  |  | ACTUAL | [7 empty] | SETPOINT |  |  |  | --- | "w.c.
RPM | [15 empty] | ACT. MEASUREMENT |  |  |  |  | "w.c.
FULL LOAD AMPS. | [7 empty] | ---
CRT. NAME AMPS. |  |  |  |  | ---
OP. AMPS. |  |  |  |  | --- | [8 empty] | SUPPLY FAN SPEED FINAL SETTING | [8 empty] | STATIC PRESSURE PROFILE SELECTIONS |  |  |  | BASIC TESTING WORKFLOW (Indicate Complete with x)
VOLTS | [27 empty] | 1
[23 empty] | A - B |  |  |  |  | 2 | Verify duct layout (areas served) vs drawings and neck sizes.
STATIC PRESSURE PROFILE "w.c. | [22 empty] | B - C |  |  |  |  | 3 | Check nameplate against submittal.
COMPONENT | [22 empty] | C - D |  |  |  |  | 4 | Open dampers and check that automatic dampers open when the system is energized.
[23 empty] | D - E |  |  |  |  | 5 | Check pulley alignment and tightness.
[23 empty] | E - F |  |  |  |  | 6 | Put the unit into full cooling.
[23 empty] | F - G |  |  |  |  | 7 | Check rotation.
PRESSURE | [22 empty] | G - H |  |  |  |  | 8 | Measure the inlets / outlets on the system.
[23 empty] | H - I |  |  |  |  | 9 | Proportion the inlets / outlets to the available airflow.
[23 empty] | I - J |  |  |  |  | 10 | Adjust rpm as needed to achieve design airflow based on rpm vs cfm equation.
| REMARKS | [21 empty] | J - K |  |  |  |  | 11 | Adjust outside and return air to design.
[28 empty] | 12 | Measure rpm, amperage and voltage.
[28 empty] | 13 | Measure inlets / outlets on the system.
[28 empty] | 14 | Record unit pressure profile (before filter, after filter, suction and discharge pressures etc.)
[28 empty] | 15 | Measure the entering and leaving chilled water pressure and set to design if applicable.
[28 empty] | 16 | Measure the entering and leaving dry and wet bulb temperatures across the cooling coil.
[28 empty] | 17 | Put the unit into full heating if applicable.
[28 empty] | 18 | Measure the total airflow and record differences to design.
[28 empty] | 19 | Measure electric heating components or heating hot water pressures and set to design.
[28 empty] | 20 | Measure entering and leaving air temperature (dry bulb only).
[27 empty] | Note - Measure total supply, return and outside airflows by traverse when possible. |  | Make sure all information on the data sheet is filled out.
TEST DATE | [10 empty] | READINGS BY
LOOKING
CCW

## RTU-PW01 - SPLYCURVE
RTU-PW01 - SUPPLY FAN CURVE PLACEHOLDER

## RTU-PW01 - RTNCURVE
RTU-PW01 - RETURN FAN CURVE PLACEHOLDER

## RTU-PW01 - SUPTRAV-VEL
INTERNAL USE ONLY - DOES NOT PRINT
SUPPLY AIR TRAVERSE TEST REPORT
PROJECT |  |  |  | EHC - Tallahassee Reno. & Add. | [15 empty] | SYSTEM |  |  | RTU-PW01
PROJECT TOLERANCES
AREA SERVED |  |  |  | Private Rooms | [15 empty] | LOCATION |  |  | Roof | [6 empty] | ABOVE DESIGN
BELOW DESIGN
TRAVERSE DATA
TRAVERSE AREA | [9 empty] | DESIGN AIRFLOW | [9 empty] | ACTUAL AIRFLOW | [8 empty] | FINAL CFM TOLERANCE CHECK
SIZE |  | "W |  |  | "H |  | SQ. FT. |  |  | FPM |  |  |  | CFM |  | 3825 |  |  |  | FPM |  |  |  |  | CFM
[12 empty] | OP. FREQ. FINAL SETTING | [7 empty] | TESTING EQUIPMENT
[20 empty] | INSTRUMENT |  |  | Air Data Multimeter - Velocity Grid
AIR VELOCITY READINGS (FPM) | [28 empty] | (W) WIDTH DISTANCE AND NO. OF POINT CALCS.
POSITION (IN.) |  |  |  |  | 1 | 2 |  | 3 | 4 |  | 5 |  | 6 | 7 |  | 8 |  | 9 |  |  | 10 | 11 |  | 12 |  | 13 | 14
NO. |  |  | POINT |  | 6 | [23 empty] | WIDTH "
1 |  |  | 6 | [25 empty] | NO. OF POINTS
2 | [28 empty] | POINT DISTANCE " | [5 empty] | GENERAL FIELD CALC. AREA
3
4 | [28 empty] | (H) HEIGHT DISTANCE AND NO. OF POINT CALCS.
5
6 | [28 empty] | HEIGHT "
7 | [28 empty] | NO. OF POINTS
8 | [28 empty] | POINT DISTANCE "
9
10 | [28 empty] | DECIMAL TO FRACTION CONVERTER (Fraction as Quarters)
SUB-TOTAL |  |  |  |  | 0 | [23 empty] | POSITION |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
[29 empty] | NO. |  | POINT | 6
| REMARKS | [17 empty] | CENTERLINE TRAVERSE SP | [7 empty] | "w.c. |  | 1 |  | 6
[19 empty] | AIR TEMPERATURE | [7 empty] | °F |  | 2
[19 empty] | TOTAL READINGS | [7 empty] | FPM |  | 3
[19 empty] | NO. READINGS | [9 empty] | 4
[19 empty] | AVG. VELOCITY | [7 empty] | FPM |  | 5
[19 empty] | EFFECTIVE AREA MULTIPLIER | [9 empty] | 6
[19 empty] | AREA | [7 empty] | SQ. FT. |  | 7
[19 empty] | TOTAL AIRFLOW | [7 empty] | CFM |  | 8
9
TEST DATE | [16 empty] | READINGS BY | [11 empty] | 10

## RTU-PW01 - SUPTRAV-PTO
INTERNAL USE ONLY - DOES NOT PRINT
SUPPLY AIR TRAVERSE TEST REPORT
PROJECT |  |  |  | EHC - Tallahassee Reno. & Add. | [17 empty] | SYSTEM |  |  | RTU-PW01
[34 empty] | PROJECT TOLERANCES | DECIMAL TO FRACTION CONVERTER (Fraction as Quarters)
AREA SERVED |  |  |  | Private Rooms | [17 empty] | LOCATION |  |  | Roof | [8 empty] | ABOVE DESIGN | POSITION (IN.) |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
[34 empty] | BELOW DESIGN | NO. | POINT
TRAVERSE DATA | [34 empty] | 1
DUCT SIZE | [9 empty] | DESIGN AIRFLOW | [11 empty] | ACTUAL AIRFLOW | [10 empty] | FINAL CFM TOLERANCE CHECK |  | 2
"W |  |  | PORT # |  |  |  | SQ. FT. |  |  | FPM |  |  |  | CFM |  |  | 3825 |  |  |  |  | FPM |  |  |  |  | CFM | [7 empty] | 3
"H |  |  | PORT # | [31 empty] | 4
[8 empty] | OP. FREQ. FINAL SETTING | [6 empty] | TESTING EQUIPMENT INSTRUMENT | [9 empty] | Air Data Multimeter - Pitot Tube | [7 empty] | (W) WIDTH DISTANCE AND NO. OF POINT CALCS. |  | 5
6
AIR VELOCITY READINGS (FPM) | [32 empty] | WIDTH " |  | 7
POSITION (IN.) | [32 empty] | NO. OF POINTS |  | 8
NO. |  | POINT | VP |  | VEL | VP | VEL | VP | VEL | VP | VEL | VP | VEL | VP |  | VEL |  | VP |  | VEL |  | VP | VEL | VP |  | VEL | VP | VEL | VP |  | VEL |  | POINT DISTANCE " |  | 9
1 | [34 empty] | 10
2 | [32 empty] | (H) HEIGHT DISTANCE AND NO. OF POINT CALCS.
3
4 | [32 empty] | HEIGHT "
5 | [32 empty] | NO. OF POINTS
6 | [32 empty] | POINT DISTANCE "
7
8 | [32 empty] | GENERAL FIELD CALC. AREA
9
10
SUB-TOTAL
REMARKS
[21 empty] | CENTERLINE TRAVERSE ("w.c.) | [6 empty] | TP |  | SP
[21 empty] | AIR TEMPERATURE | [8 empty] | °F
[21 empty] | TOTAL READINGS | [8 empty] | FPM |  |  | If you have a VP that is 0.00 you need to unlock the sheet and adjust ALL VP
NO. READINGS
[21 empty] | AVG. VELOCITY | [8 empty] | FPM |  |  | columns to the thousandth decimal place and re-enter the traverse with three digits.
EFFECTIVE AREA MULTIPLIER
[21 empty] | AREA | [8 empty] | SQ. FT. |  |  | In most cases a 0.00 will move to a 0.002 or a 0.001 etc. A legitimate zero VP (0.00 or 0.000) is a
[21 empty] | TOTAL AIRFLOW | [8 empty] | CFM |  |  | red flag in report reviews. Note: Do not adjust the decimal place for the "VEL" columns.
TEST DATE | [18 empty] | READINGS BY

## RTU-PW01 - SUPTRAV-RNDPTO
INTERNAL USE ONLY - DOES NOT PRINT
SUPPLY AIR TRAVERSE TEST REPORT
PROJECT |  |  |  | EHC - Tallahassee Reno. & Add. | [13 empty] | SYSTEM | RTU-PW01
PROJECT TOLERANCES
AREA SERVED |  |  |  | Private Rooms | [13 empty] | LOCATION | Roof | [5 empty] | ABOVE DESIGN
BELOW DESIGN
TRAVERSE DATA
TRAVERSE AREA | [10 empty] | DESIGN AIRFLOW | [6 empty] | ACTUAL AIRFLOW | [5 empty] | FINAL CFM TOLERANCE CHECK
SIZE |  |  | " ROUND |  |  | SQ. FT. |  | 0 |  |  | FPM |  | CFM |  | 3825 |  |  | FPM |  | CFM
AIR VELOCITY READINGS (FPM) | [11 empty] | OP. FREQ. FINAL SETTING | [5 empty] | TESTING EQUIPMENT | [5 empty] | GENERAL FIELD CALC. AREA
POSITION |  |  |  |  | X AXIS |  |  |  | Y AXIS | [8 empty] | INSTRUMENT | Air Data Multimeter - Pitot Tube
NO. |  | POINT |  |  | VP |  | VEL |  | VP | VEL
1 |  | 0
2 |  | 0
3 |  | 0
4 |  | 0
5 |  | 0
6 |  | 0
7 |  | 0
8 |  | 0
9 |  | 0
10 |  | 0
SUB-TOTAL |  |  |  |  | --- |  |  |  | ---
| REMARKS | [15 empty] | CENTERLINE TRAVERSE SP |  |  |  |  | "w.c. |  | If you have a VP that is 0.00 you need to unlock the sheet and adjust ALL VP
[17 empty] | AIR TEMPERATURE |  |  |  |  | °F
[17 empty] | TOTAL READINGS |  |  |  | 0 | FPM |  | columns to the thousandth decimal place and re-enter the traverse with three digits.
[17 empty] | NO. READINGS |  |  |  | 0
[17 empty] | AVG. VELOCITY |  |  |  |  | FPM |  | In most cases a 0.00 will move to a 0.002 or a 0.001 etc. A legitimate zero VP (0.00 or 0.000) is a
[17 empty] | EFFECTIVE AREA MULTIPLIER | [6 empty] | red flag in report reviews. Note: Do not adjust the decimal place for the "VEL" columns.
[17 empty] | AREA |  |  |  | 0 | SQ. FT.
[17 empty] | TOTAL AIRFLOW |  |  |  |  | CFM
TEST DATE | [15 empty] | READINGS BY
X AXIS
Y AXIS

## RTU-PW01 - OATRAV-VEL
INTERNAL USE ONLY - DOES NOT PRINT
OUTSIDE AIR TRAVERSE TEST REPORT
PROJECT |  |  |  | EHC - Tallahassee Reno. & Add. | [15 empty] | SYSTEM |  |  | RTU-PW01
PROJECT TOLERANCES
AREA SERVED |  |  |  | Private Rooms | [15 empty] | LOCATION |  |  | Roof | [6 empty] | ABOVE DESIGN
BELOW DESIGN
TRAVERSE DATA
TRAVERSE AREA | [9 empty] | DESIGN AIRFLOW | [9 empty] | ACTUAL AIRFLOW | [8 empty] | FINAL CFM TOLERANCE CHECK
SIZE |  | "W |  |  | "H |  | SQ. FT. |  |  | FPM |  |  |  | CFM |  | 1148 |  |  |  | FPM |  |  |  |  | CFM
[12 empty] | OP. FREQ. FINAL SETTING | [7 empty] | TESTING EQUIPMENT
[20 empty] | INSTRUMENT |  |  | Air Data Multimeter - Velocity Grid
AIR VELOCITY READINGS (FPM) | [28 empty] | (W) WIDTH DISTANCE AND NO. OF POINT CALCS.
POSITION (IN.) |  |  |  |  | 1 | 2 |  | 3 | 4 |  | 5 |  | 6 | 7 |  | 8 |  | 9 |  |  | 10 | 11 |  | 12 |  | 13 | 14
NO. |  |  | POINT |  | 6 | [23 empty] | WIDTH "
1 |  |  | 6 | [25 empty] | NO. OF POINTS
2 | [28 empty] | POINT DISTANCE " | [5 empty] | GENERAL FIELD CALC. AREA
3
4 | [28 empty] | (H) HEIGHT DISTANCE AND NO. OF POINT CALCS.
5
6 | [28 empty] | HEIGHT "
7 | [28 empty] | NO. OF POINTS
8 | [28 empty] | POINT DISTANCE "
9
10 | [28 empty] | DECIMAL TO FRACTION CONVERTER (Fraction as Quarters)
SUB-TOTAL |  |  |  |  | 0 | [23 empty] | POSITION |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
[29 empty] | NO. |  | POINT | 6
| REMARKS | [17 empty] | CENTERLINE TRAVERSE SP | [7 empty] | "w.c. |  | 1 |  | 6
[19 empty] | AIR TEMPERATURE | [7 empty] | °F |  | 2
[19 empty] | TOTAL READINGS | [7 empty] | FPM |  | 3
[19 empty] | NO. READINGS | [9 empty] | 4
[19 empty] | AVG. VELOCITY | [7 empty] | FPM |  | 5
[19 empty] | EFFECTIVE AREA MULTIPLIER | [9 empty] | 6
[19 empty] | AREA | [7 empty] | SQ. FT. |  | 7
[19 empty] | TOTAL AIRFLOW | [7 empty] | CFM |  | 8
9
TEST DATE | [16 empty] | READINGS BY | [11 empty] | 10

## RTU-PW01 - OATRAV-PTO
INTERNAL USE ONLY - DOES NOT PRINT
OUTSIDE AIR TRAVERSE TEST REPORT
PROJECT |  |  |  | EHC - Tallahassee Reno. & Add. | [17 empty] | SYSTEM |  |  | RTU-PW01
[34 empty] | PROJECT TOLERANCES | DECIMAL TO FRACTION CONVERTER (Fraction as Quarters)
AREA SERVED |  |  |  | Private Rooms | [17 empty] | LOCATION |  |  | Roof | [8 empty] | ABOVE DESIGN | POSITION (IN.) |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
[34 empty] | BELOW DESIGN | NO. | POINT
TRAVERSE DATA | [34 empty] | 1
DUCT SIZE | [9 empty] | DESIGN AIRFLOW | [11 empty] | ACTUAL AIRFLOW | [10 empty] | FINAL CFM TOLERANCE CHECK |  | 2
"W |  |  | PORT # |  |  |  | SQ. FT. |  |  | FPM |  |  |  | CFM |  |  | 1148 |  |  |  |  | FPM |  |  |  |  | CFM | [7 empty] | 3
"H |  |  | PORT # | [31 empty] | 4
[8 empty] | OP. FREQ. FINAL SETTING | [6 empty] | TESTING EQUIPMENT INSTRUMENT | [9 empty] | Air Data Multimeter - Pitot Tube | [7 empty] | (W) WIDTH DISTANCE AND NO. OF POINT CALCS. |  | 5
6
AIR VELOCITY READINGS (FPM) | [32 empty] | WIDTH " |  | 7
POSITION (IN.) | [32 empty] | NO. OF POINTS |  | 8
NO. |  | POINT | VP |  | VEL | VP | VEL | VP | VEL | VP | VEL | VP | VEL | VP |  | VEL |  | VP |  | VEL |  | VP | VEL | VP |  | VEL | VP | VEL | VP |  | VEL |  | POINT DISTANCE " |  | 9
1 | [34 empty] | 10
2 | [32 empty] | (H) HEIGHT DISTANCE AND NO. OF POINT CALCS.
3
4 | [32 empty] | HEIGHT "
5 | [32 empty] | NO. OF POINTS
6 | [32 empty] | POINT DISTANCE "
7
8 | [32 empty] | GENERAL FIELD CALC. AREA
9
10
SUB-TOTAL
REMARKS
[21 empty] | CENTERLINE TRAVERSE ("w.c.) | [6 empty] | TP |  | SP
[21 empty] | AIR TEMPERATURE | [8 empty] | °F
[21 empty] | TOTAL READINGS | [8 empty] | FPM |  |  | If you have a VP that is 0.00 you need to unlock the sheet and adjust ALL VP
NO. READINGS
[21 empty] | AVG. VELOCITY | [8 empty] | FPM |  |  | columns to the thousandth decimal place and re-enter the traverse with three digits.
EFFECTIVE AREA MULTIPLIER
[21 empty] | AREA | [8 empty] | SQ. FT. |  |  | In most cases a 0.00 will move to a 0.002 or a 0.001 etc. A legitimate zero VP (0.00 or 0.000) is a
[21 empty] | TOTAL AIRFLOW | [8 empty] | CFM |  |  | red flag in report reviews. Note: Do not adjust the decimal place for the "VEL" columns.
TEST DATE | [18 empty] | READINGS BY

## RTU-PW01 - OATRAV-RNDPTO
INTERNAL USE ONLY - DOES NOT PRINT
OUTSIDE AIR TRAVERSE TEST REPORT
PROJECT |  |  |  | EHC - Tallahassee Reno. & Add. | [13 empty] | SYSTEM | RTU-PW01
PROJECT TOLERANCES
AREA SERVED |  |  |  | Private Rooms | [13 empty] | LOCATION | Roof | [5 empty] | ABOVE DESIGN
BELOW DESIGN
TRAVERSE DATA
TRAVERSE AREA | [10 empty] | DESIGN AIRFLOW | [6 empty] | ACTUAL AIRFLOW | [5 empty] | FINAL CFM TOLERANCE CHECK
SIZE |  |  | " ROUND |  |  | SQ. FT. |  | 0 |  |  | FPM |  | CFM |  | 1148 |  |  | FPM |  | CFM
AIR VELOCITY READINGS (FPM) | [11 empty] | OP. FREQ. FINAL SETTING | [5 empty] | TESTING EQUIPMENT | [5 empty] | GENERAL FIELD CALC. AREA
POSITION |  |  |  |  | X AXIS |  |  |  | Y AXIS | [8 empty] | INSTRUMENT | Air Data Multimeter - Pitot Tube
NO. |  | POINT |  |  | VP |  | VEL |  | VP | VEL
1 |  | 0
2 |  | 0
3 |  | 0
4 |  | 0
5 |  | 0
6 |  | 0
7 |  | 0
8 |  | 0
9 |  | 0
10 |  | 0
SUB-TOTAL |  |  |  |  | --- |  |  |  | ---
| REMARKS | [15 empty] | CENTERLINE TRAVERSE SP |  |  |  |  | "w.c. |  | If you have a VP that is 0.00 you need to unlock the sheet and adjust ALL VP
[17 empty] | AIR TEMPERATURE |  |  |  |  | °F
[17 empty] | TOTAL READINGS |  |  |  | 0 | FPM |  | columns to the thousandth decimal place and re-enter the traverse with three digits.
[17 empty] | NO. READINGS |  |  |  | 0
[17 empty] | AVG. VELOCITY |  |  |  |  | FPM |  | In most cases a 0.00 will move to a 0.002 or a 0.001 etc. A legitimate zero VP (0.00 or 0.000) is a
[17 empty] | EFFECTIVE AREA MULTIPLIER | [6 empty] | red flag in report reviews. Note: Do not adjust the decimal place for the "VEL" columns.
[17 empty] | AREA |  |  |  | 0 | SQ. FT.
[17 empty] | TOTAL AIRFLOW |  |  |  |  | CFM
TEST DATE | [15 empty] | READINGS BY
X AXIS
Y AXIS

## RTU-PW01 - RTNTRAV-VEL
INTERNAL USE ONLY - DOES NOT PRINT
RETURN AIR TRAVERSE TEST REPORT
PROJECT |  |  |  | EHC - Tallahassee Reno. & Add. | [15 empty] | SYSTEM |  |  | RTU-PW01
PROJECT TOLERANCES
AREA SERVED |  |  |  | Private Rooms | [15 empty] | LOCATION |  |  | Roof | [6 empty] | ABOVE DESIGN
BELOW DESIGN
TRAVERSE DATA
TRAVERSE AREA | [9 empty] | DESIGN AIRFLOW | [9 empty] | ACTUAL AIRFLOW | [8 empty] | FINAL CFM TOLERANCE CHECK
SIZE |  | "W |  |  | "H |  | SQ. FT. |  |  | FPM |  |  |  | CFM | [5 empty] | FPM |  |  |  |  | CFM
[12 empty] | OP. FREQ. FINAL SETTING | [7 empty] | TESTING EQUIPMENT
[20 empty] | INSTRUMENT |  |  | Air Data Multimeter - Velocity Grid
AIR VELOCITY READINGS (FPM) | [28 empty] | (W) WIDTH DISTANCE AND NO. OF POINT CALCS.
POSITION (IN.) |  |  |  |  | 1 | 2 |  | 3 | 4 |  | 5 |  | 6 | 7 |  | 8 |  | 9 |  |  | 10 | 11 |  | 12 |  | 13 | 14
NO. |  |  | POINT |  | 6 | [23 empty] | WIDTH "
1 |  |  | 6 | [25 empty] | NO. OF POINTS
2 | [28 empty] | POINT DISTANCE " | [5 empty] | GENERAL FIELD CALC. AREA
3
4 | [28 empty] | (H) HEIGHT DISTANCE AND NO. OF POINT CALCS.
5
6 | [28 empty] | HEIGHT "
7 | [28 empty] | NO. OF POINTS
8 | [28 empty] | POINT DISTANCE "
9
10 | [28 empty] | DECIMAL TO FRACTION CONVERTER (Fraction as Quarters)
SUB-TOTAL |  |  |  |  | 0 | [23 empty] | POSITION |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
[29 empty] | NO. |  | POINT | 6
| REMARKS | [17 empty] | CENTERLINE TRAVERSE SP | [7 empty] | "w.c. |  | 1 |  | 6
[19 empty] | AIR TEMPERATURE | [7 empty] | °F |  | 2
[19 empty] | TOTAL READINGS | [7 empty] | FPM |  | 3
[19 empty] | NO. READINGS | [9 empty] | 4
[19 empty] | AVG. VELOCITY | [7 empty] | FPM |  | 5
[19 empty] | EFFECTIVE AREA MULTIPLIER | [9 empty] | 6
[19 empty] | AREA | [7 empty] | SQ. FT. |  | 7
[19 empty] | TOTAL AIRFLOW | [7 empty] | CFM |  | 8
9
TEST DATE | [16 empty] | READINGS BY | [11 empty] | 10

## RTU-PW01 - RTNTRAV-PTO
INTERNAL USE ONLY - DOES NOT PRINT
RETURN AIR TRAVERSE TEST REPORT
PROJECT |  |  |  | EHC - Tallahassee Reno. & Add. | [16 empty] | SYSTEM |  |  | RTU-PW01
[33 empty] | PROJECT TOLERANCES | DECIMAL TO FRACTION CONVERTER (Fraction as Quarters)
AREA SERVED |  |  |  | Private Rooms | [16 empty] | LOCATION |  |  | Roof | [8 empty] | ABOVE DESIGN | POSITION (IN.) |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
[33 empty] | BELOW DESIGN | NO. | POINT
TRAVERSE DATA | [33 empty] | 1
DUCT SIZE | [9 empty] | DESIGN AIRFLOW | [10 empty] | ACTUAL AIRFLOW | [10 empty] | FINAL CFM TOLERANCE CHECK |  | 2
"W |  |  | PORT # |  |  |  | SQ. FT. |  |  | FPM |  |  |  | CFM | [6 empty] | FPM |  |  |  |  | CFM | [7 empty] | 3
"H |  |  | PORT # | [30 empty] | 4
[8 empty] | OP. FREQ. FINAL SETTING | [6 empty] | TESTING EQUIPMENT INSTRUMENT | [8 empty] | Air Data Multimeter - Pitot Tube | [7 empty] | (W) WIDTH DISTANCE AND NO. OF POINT CALCS. |  | 5
6
AIR VELOCITY READINGS (FPM) | [31 empty] | WIDTH " |  | 7
POSITION (IN.) | [31 empty] | NO. OF POINTS |  | 8
NO. |  | POINT | VP |  | VEL | VP | VEL | VP | VEL | VP | VEL | VP | VEL | VP |  | VEL | VP |  | VEL |  | VP | VEL | VP |  | VEL | VP | VEL | VP |  | VEL |  | POINT DISTANCE " |  | 9
1 | [33 empty] | 10
2 | [31 empty] | (H) HEIGHT DISTANCE AND NO. OF POINT CALCS.
3
4 | [31 empty] | HEIGHT "
5 | [31 empty] | NO. OF POINTS
6 | [31 empty] | POINT DISTANCE "
7
8 | [31 empty] | GENERAL FIELD CALC. AREA
9
10
SUB-TOTAL
REMARKS
[20 empty] | CENTERLINE TRAVERSE ("w.c.) | [6 empty] | TP |  | SP
[20 empty] | AIR TEMPERATURE | [8 empty] | °F
[20 empty] | TOTAL READINGS | [8 empty] | FPM |  |  | If you have a VP that is 0.00 you need to unlock the sheet and adjust ALL VP
NO. READINGS
[20 empty] | AVG. VELOCITY | [8 empty] | FPM |  |  | columns to the thousandth decimal place and re-enter the traverse with three digits.
EFFECTIVE AREA MULTIPLIER
[20 empty] | AREA | [8 empty] | SQ. FT. |  |  | In most cases a 0.00 will move to a 0.002 or a 0.001 etc. A legitimate zero VP (0.00 or 0.000) is a
[20 empty] | TOTAL AIRFLOW | [8 empty] | CFM |  |  | red flag in report reviews. Note: Do not adjust the decimal place for the "VEL" columns.
TEST DATE | [17 empty] | READINGS BY

## RTU-PW01 - RTNTRAV-RNDPTO
INTERNAL USE ONLY - DOES NOT PRINT
RETURN AIR TRAVERSE TEST REPORT
PROJECT |  |  |  | EHC - Tallahassee Reno. & Add. | [12 empty] | SYSTEM | RTU-PW01
PROJECT TOLERANCES
AREA SERVED |  |  |  | Private Rooms | [12 empty] | LOCATION | Roof | [5 empty] | ABOVE DESIGN
BELOW DESIGN
TRAVERSE DATA
TRAVERSE AREA | [10 empty] | DESIGN AIRFLOW | [5 empty] | ACTUAL AIRFLOW | [5 empty] | FINAL CFM TOLERANCE CHECK
SIZE |  |  | " ROUND |  |  | SQ. FT. |  | 0 |  |  | FPM |  | CFM |  |  |  | FPM |  | CFM
AIR VELOCITY READINGS (FPM) | [11 empty] | OP. FREQ. FINAL SETTING |  |  |  |  | TESTING EQUIPMENT | [5 empty] | GENERAL FIELD CALC. AREA
POSITION |  |  |  |  | X AXIS |  |  |  | Y AXIS | [7 empty] | INSTRUMENT | Air Data Multimeter - Pitot Tube
NO. |  | POINT |  |  | VP |  | VEL |  | VP | VEL
1 |  | 0
2 |  | 0
3 |  | 0
4 |  | 0
5 |  | 0
6 |  | 0
7 |  | 0
8 |  | 0
9 |  | 0
10 |  | 0
SUB-TOTAL |  |  |  |  | --- |  |  |  | ---
| REMARKS | [14 empty] | CENTERLINE TRAVERSE SP |  |  |  |  | "w.c. |  | If you have a VP that is 0.00 you need to unlock the sheet and adjust ALL VP
[16 empty] | AIR TEMPERATURE |  |  |  |  | °F
[16 empty] | TOTAL READINGS |  |  |  | 0 | FPM |  | columns to the thousandth decimal place and re-enter the traverse with three digits.
[16 empty] | NO. READINGS |  |  |  | 0
[16 empty] | AVG. VELOCITY |  |  |  |  | FPM |  | In most cases a 0.00 will move to a 0.002 or a 0.001 etc. A legitimate zero VP (0.00 or 0.000) is a
[16 empty] | EFFECTIVE AREA MULTIPLIER | [6 empty] | red flag in report reviews. Note: Do not adjust the decimal place for the "VEL" columns.
[16 empty] | AREA |  |  |  | 0 | SQ. FT.
[16 empty] | TOTAL AIRFLOW |  |  |  |  | CFM
TEST DATE | [14 empty] | READINGS BY
X AXIS
Y AXIS

## RTU-PW01 - INLETSUM-1
INTERNAL USE ONLY - DOES NOT PRINT
DUCTED RETURN TEST REPORT
PROJECT |  | EHC - Tallahassee Reno. & Add. | [5 empty] | SYSTEM |  | RTU-PW01
PROJECT TOLERANCES
[17 empty] | ABOVE DESIGN | GENERAL FIELD CALC. AREA
[15 empty] | FOR PROPORTIONS, CORRECTION FACTORS, ETC. |  | BELOW DESIGN
AREA SERVED LOCATION |  |  | INLETS |  |  |  | DESIGN CFM | PRELIMINARY CFM |  |  |  | FINAL CFM | REMARKS
|  |  | NO. | TYPE |  | SIZE (IN.) |  | TEST1 | TEST 2 |  | TEST 3 |  |  |  |  | FINAL CFM TOLERANCE CHECK
Private F154 |  |  | 1 | CRG1 |  | 10 | 200
Clean Hold F101 |  |  | 2 | " |  | " | 160
Corridor F105 |  |  | 3 | " |  | 12 | 350
Private F112 |  |  | 4 | " |  | 10 | 200
Private F113 |  |  | 5 | " |  | " | 200
Private F114 |  |  | 6 | " |  | " | 200
Private F115 |  |  | 7 | " |  | " | 200
Private F116 |  |  | 8 | " |  | 8 | 145
Private F117 |  |  | 9 | " |  | " | 145
Corridor F105 |  |  | 10 | " |  | 12 | 355
Private F118 |  |  | 11 | " |  | 10 | 200
Private F119 |  |  | 12 | " |  | " | 200
TOTAL | [6 empty] | 2555
2555
REMARKS
TEST DATE | [6 empty] | READINGS BY

## RTU-PW01 - ATUSUM
INTERNAL USE ONLY - DOES NOT PRINT
AIR TERMINAL UNIT SUMMARY REPORT
PROJECT |  | EHC - Tallahassee Reno. & Add. | [9 empty] | SYSTEM |  | RTU-PW01
AIR TERMINAL UNIT DATA | [17 empty] | GENERAL FIELD CALC. AREA
AIR TERMINAL NO. |  |  | AIRFLOW |  |  |  | FAN |  | HEATING |  | CALIBRATION DATA |  |  |  |  | REMARKS
|  |  | DESIGN MAX. | ACTUAL MAX. | DESIGN MIN. | ACTUAL MIN. | DESIGN FAN | ACTUAL FAN | DESIGN HEAT MAX | ACTUAL HEAT MAX | CALIBRATION CODE |  | INLET SIZE (IN.) |  | DDC. ADDRESS
VAV-PW-01 |  |  | 390 |  | 240 | 0 | --- | --- | 240 | 0 | 0 |  | 0 |  | 0
VAV-PW-02 |  |  | 300 |  | 180 | 0 | --- | --- | 180 | 0 | 0 |  | 0 |  | 0
VAV-PW-03 |  |  | 430 |  | 260 | 0 | --- | --- | 260 | 0 | 0 |  | 8 |  | 0
VAV-PW-04 |  |  | 430 |  | 260 | 0 | --- | --- | 260 | 0 | 0 |  | 8 |  | 0
VAV-PW-05 |  |  | 400 |  | 240 | 0 | --- | --- | 240 | 0 | 0 |  | 0 |  | 0
VAV-PW-06 |  |  | 300 |  | 180 | 0 | --- | --- | 180 | 0 | 0 |  | 0 |  | 0
VAV-PW-13 |  |  | 300 |  | 180 | 0 | --- | --- | 180 | 0 | 0 |  | 0 |  | 0
VAV-PW-14 |  |  | 350 |  | 210 | 0 | --- | --- | 210 | 0 | 0 |  | 0 |  | 0
VAV-PW-15 |  |  | 300 |  | 180 | 0 | --- | --- | 180 | 0 | 0 |  | 0 |  | 0
VAV-PW-22 |  |  | 100 |  | 60 | 0 | --- | --- | --- | 0 | 0 |  | 6 |  | 0
VAV-PW-23 |  |  | 325 |  | 200 | 0 | --- | --- | 200 | 0 | 0 |  | 6 |  | 0
VAV-PW-24 |  |  | 200 |  | 120 | 0 | --- | --- | 120 | 0 | 0 |  | 6 |  | 0
TOTAL |  |  | 3825 | 0 | 2310 | 0 | 0 | 0 | 2250 | 0
|  |  | 3825 | 0 | 2310 | 0 | 0 | 0 | 2250 | 0
REMARKS

## VAV-PW-01
INTERNAL USE ONLY - DOES NOT PRINT
VARIABLE AIR VOLUME UNIT TEST REPORT
PROJECT | EHC - Tallahassee Reno. & Add. | [7 empty] | SYSTEM |  | RTU-PW01 | [5 empty] | BASIC TESTING WORKFLOW (Indicate Complete with x) | [5 empty] | TIME TO COMPLETE STEPS (MINS.)
[23 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42
AREA SERVED | Private F114 | [7 empty] | LOCATION |  | Corridor F105 | [6 empty] | 1 | Get controls communicating. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
[18 empty] | 2 | Verify duct layout vs drawings with neck size. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
VAV UNIT DATA | [8 empty] | VAV PERFORMANCE DATA | [8 empty] | 3 | Open dampers. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 10
VAV # |  | VAV-PW-01 | [9 empty] | DESIGN |  | ACTUAL |  |  |  | 4 | Put box in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 7
INLET SIZE |  |  |  |  | " | Round |  |  | CLG. MAX. CFM |  |  | 390 | [5 empty] | 5 | Nameplate check against submittal. | bar: TIME TO COMPLETE STEPS (MINS.) 8 to TIME TO COMPLETE STEPS (MINS.) 10
MFG. | [8 empty] | CLG. MIN. CFM |  |  | 240 | [5 empty] | 6 | Measure outlets in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 11 to TIME TO COMPLETE STEPS (MINS.) 15
TYPE |  | VAV | [6 empty] | HTG. MAX. CFM |  |  | 240 | [5 empty] | 7 | Calibrate flow at max. | bar: TIME TO COMPLETE STEPS (MINS.) 16 to TIME TO COMPLETE STEPS (MINS.) 17
MODEL NO. | [8 empty] | HTG. MIN. CFM |  |  | --- | [5 empty] | 8 | Balance at calibrated max w/ double check readings. | bar: TIME TO COMPLETE STEPS (MINS.) 18 to TIME TO COMPLETE STEPS (MINS.) 27
SERVICE |  | Conditioned Air | [15 empty] | 9 | Put box to satisfied. | bar: TIME TO COMPLETE STEPS (MINS.) 28 to TIME TO COMPLETE STEPS (MINS.) 29
SERIAL NO. | [17 empty] | 10 | Measure outlets in satisfied condition, record flow. | bar: TIME TO COMPLETE STEPS (MINS.) 30 to TIME TO COMPLETE STEPS (MINS.) 32
DDC TERMINAL # | [17 empty] | 11 | Put box in heat. | bar: TIME TO COMPLETE STEPS (MINS.) 33 to TIME TO COMPLETE STEPS (MINS.) 34
COR. FACTOR | [17 empty] | 12 | Measure outlets and record total. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 2: LEGEND
[18 empty] | 13 | Measure elec. heat components (or water). |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: EIT
[18 empty] | 14 | Measure LAT. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TECH
[18 empty] | 15 | Release the box. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TEAM
[18 empty] | 16 | Make sure all information on the data sheet is filled out.
[21 empty] | PROJECT TOLERANCES | GENERAL FIELD CALC. AREA
ABOVE DESIGN
[17 empty] | FOR PROPORTIONS, CORRECTION FACTORS, ETC. |  |  |  | BELOW DESIGN
AREA SERVED LOCATION |  |  | OUTLETS |  |  |  |  | DESIGN CFM | PRELIMINARY CFM |  |  |  | FINAL CFM |  | REMARKS
|  |  | NO. | TYPE |  |  | SIZE (IN.) |  | TEST1 | TEST 2 |  | TEST 3 | [7 empty] | FINAL CFM TOLERANCE CHECK
Private F114 |  |  | 1 | CSD1 |  |  | 10 | 300
Corridor F105 |  |  | 2 | " |  |  | 6 | 50
TOTAL | [7 empty] | 350
REMARKS
TEST DATE | [7 empty] | READINGS BY

## VAV-PW-02
INTERNAL USE ONLY - DOES NOT PRINT
VARIABLE AIR VOLUME UNIT TEST REPORT
PROJECT | EHC - Tallahassee Reno. & Add. | [7 empty] | SYSTEM |  | RTU-PW01 | [5 empty] | BASIC TESTING WORKFLOW (Indicate Complete with x) | [5 empty] | TIME TO COMPLETE STEPS (MINS.)
[23 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42
AREA SERVED | Private F115 | [7 empty] | LOCATION |  | Corridor F105 | [6 empty] | 1 | Get controls communicating. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
[18 empty] | 2 | Verify duct layout vs drawings with neck size. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
VAV UNIT DATA | [8 empty] | VAV PERFORMANCE DATA | [8 empty] | 3 | Open dampers. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 10
VAV # |  | VAV-PW-02 | [9 empty] | DESIGN |  | ACTUAL |  |  |  | 4 | Put box in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 7
INLET SIZE |  |  |  |  | " | Round |  |  | CLG. MAX. CFM |  |  | 300 | [5 empty] | 5 | Nameplate check against submittal. | bar: TIME TO COMPLETE STEPS (MINS.) 8 to TIME TO COMPLETE STEPS (MINS.) 10
MFG. | [8 empty] | CLG. MIN. CFM |  |  | 180 | [5 empty] | 6 | Measure outlets in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 11 to TIME TO COMPLETE STEPS (MINS.) 15
TYPE |  | VAV | [6 empty] | HTG. MAX. CFM |  |  | 180 | [5 empty] | 7 | Calibrate flow at max. | bar: TIME TO COMPLETE STEPS (MINS.) 16 to TIME TO COMPLETE STEPS (MINS.) 17
MODEL NO. | [8 empty] | HTG. MIN. CFM |  |  | --- | [5 empty] | 8 | Balance at calibrated max w/ double check readings. | bar: TIME TO COMPLETE STEPS (MINS.) 18 to TIME TO COMPLETE STEPS (MINS.) 27
SERVICE |  | Conditioned Air | [15 empty] | 9 | Put box to satisfied. | bar: TIME TO COMPLETE STEPS (MINS.) 28 to TIME TO COMPLETE STEPS (MINS.) 29
SERIAL NO. | [17 empty] | 10 | Measure outlets in satisfied condition, record flow. | bar: TIME TO COMPLETE STEPS (MINS.) 30 to TIME TO COMPLETE STEPS (MINS.) 32
DDC TERMINAL # | [17 empty] | 11 | Put box in heat. | bar: TIME TO COMPLETE STEPS (MINS.) 33 to TIME TO COMPLETE STEPS (MINS.) 34
COR. FACTOR | [17 empty] | 12 | Measure outlets and record total. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 2: LEGEND
[18 empty] | 13 | Measure elec. heat components (or water). |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: EIT
[18 empty] | 14 | Measure LAT. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TECH
[18 empty] | 15 | Release the box. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TEAM
[18 empty] | 16 | Make sure all information on the data sheet is filled out.
[21 empty] | PROJECT TOLERANCES | GENERAL FIELD CALC. AREA
ABOVE DESIGN
[17 empty] | FOR PROPORTIONS, CORRECTION FACTORS, ETC. |  |  |  | BELOW DESIGN
AREA SERVED LOCATION |  |  | OUTLETS |  |  |  |  | DESIGN CFM | PRELIMINARY CFM |  |  |  | FINAL CFM |  | REMARKS
|  |  | NO. | TYPE |  |  | SIZE (IN.) |  | TEST1 | TEST 2 |  | TEST 3 | [7 empty] | FINAL CFM TOLERANCE CHECK
Private F115 |  |  | 1 | CSD1 |  |  | 10 | 300
TOTAL | [7 empty] | 300
REMARKS
TEST DATE | [7 empty] | READINGS BY

## VAV-PW-03
INTERNAL USE ONLY - DOES NOT PRINT
VARIABLE AIR VOLUME UNIT TEST REPORT
PROJECT | EHC - Tallahassee Reno. & Add. | [7 empty] | SYSTEM |  | RTU-PW01 | [5 empty] | BASIC TESTING WORKFLOW (Indicate Complete with x) | [5 empty] | TIME TO COMPLETE STEPS (MINS.)
[23 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42
AREA SERVED | Patient Room F116 | [7 empty] | LOCATION |  | Patient Room F116 | [6 empty] | 1 | Get controls communicating. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
[18 empty] | 2 | Verify duct layout vs drawings with neck size. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
VAV UNIT DATA | [8 empty] | VAV PERFORMANCE DATA | [8 empty] | 3 | Open dampers. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 10
VAV # |  | VAV-PW-03 | [9 empty] | DESIGN |  | ACTUAL |  |  |  | 4 | Put box in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 7
INLET SIZE |  | 8 |  |  | " | Round |  |  | CLG. MAX. CFM |  |  | 430 | [5 empty] | 5 | Nameplate check against submittal. | bar: TIME TO COMPLETE STEPS (MINS.) 8 to TIME TO COMPLETE STEPS (MINS.) 10
MFG. |  | JCI | [6 empty] | CLG. MIN. CFM |  |  | 260 | [5 empty] | 6 | Measure outlets in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 11 to TIME TO COMPLETE STEPS (MINS.) 15
TYPE |  | VAV | [6 empty] | HTG. MAX. CFM |  |  | 260 | [5 empty] | 7 | Calibrate flow at max. | bar: TIME TO COMPLETE STEPS (MINS.) 16 to TIME TO COMPLETE STEPS (MINS.) 17
MODEL NO. |  | TSS08 | [6 empty] | HTG. MIN. CFM |  |  | --- | [5 empty] | 8 | Balance at calibrated max w/ double check readings. | bar: TIME TO COMPLETE STEPS (MINS.) 18 to TIME TO COMPLETE STEPS (MINS.) 27
SERVICE |  | Conditioned Air | [15 empty] | 9 | Put box to satisfied. | bar: TIME TO COMPLETE STEPS (MINS.) 28 to TIME TO COMPLETE STEPS (MINS.) 29
SERIAL NO. | [17 empty] | 10 | Measure outlets in satisfied condition, record flow. | bar: TIME TO COMPLETE STEPS (MINS.) 30 to TIME TO COMPLETE STEPS (MINS.) 32
DDC TERMINAL # | [17 empty] | 11 | Put box in heat. | bar: TIME TO COMPLETE STEPS (MINS.) 33 to TIME TO COMPLETE STEPS (MINS.) 34
COR. FACTOR | [17 empty] | 12 | Measure outlets and record total. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 2: LEGEND
[18 empty] | 13 | Measure elec. heat components (or water). |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: EIT
[18 empty] | 14 | Measure LAT. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TECH
[18 empty] | 15 | Release the box. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TEAM
[18 empty] | 16 | Make sure all information on the data sheet is filled out.
[21 empty] | PROJECT TOLERANCES | GENERAL FIELD CALC. AREA
ABOVE DESIGN
[17 empty] | FOR PROPORTIONS, CORRECTION FACTORS, ETC. |  |  |  | BELOW DESIGN
AREA SERVED LOCATION |  |  | OUTLETS |  |  |  |  | DESIGN CFM | PRELIMINARY CFM |  |  |  | FINAL CFM |  | REMARKS
|  |  | NO. | TYPE |  |  | SIZE (IN.) |  | TEST1 | TEST 2 |  | TEST 3 | [7 empty] | FINAL CFM TOLERANCE CHECK
Patient Room F116 |  |  | 1 | CSD1 |  |  | 10 | 350
Pat. Tlt. F116A |  |  | 2 | CSD2 |  |  | 6 | 80
TOTAL | [7 empty] | 430
REMARKS
TEST DATE | [7 empty] | READINGS BY

## VAV-PW-04
INTERNAL USE ONLY - DOES NOT PRINT
VARIABLE AIR VOLUME UNIT TEST REPORT
PROJECT | EHC - Tallahassee Reno. & Add. | [7 empty] | SYSTEM |  | RTU-PW01 | [5 empty] | BASIC TESTING WORKFLOW (Indicate Complete with x) | [5 empty] | TIME TO COMPLETE STEPS (MINS.)
[23 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42
AREA SERVED | Patient Room F117 | [7 empty] | LOCATION |  | Patient Room F117 | [6 empty] | 1 | Get controls communicating. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
[18 empty] | 2 | Verify duct layout vs drawings with neck size. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
VAV UNIT DATA | [8 empty] | VAV PERFORMANCE DATA | [8 empty] | 3 | Open dampers. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 10
VAV # |  | VAV-PW-04 | [9 empty] | DESIGN |  | ACTUAL |  |  |  | 4 | Put box in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 7
INLET SIZE |  | 8 |  |  | " | Round |  |  | CLG. MAX. CFM |  |  | 430 | [5 empty] | 5 | Nameplate check against submittal. | bar: TIME TO COMPLETE STEPS (MINS.) 8 to TIME TO COMPLETE STEPS (MINS.) 10
MFG. |  | JCI | [6 empty] | CLG. MIN. CFM |  |  | 260 | [5 empty] | 6 | Measure outlets in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 11 to TIME TO COMPLETE STEPS (MINS.) 15
TYPE |  | VAV | [6 empty] | HTG. MAX. CFM |  |  | 260 | [5 empty] | 7 | Calibrate flow at max. | bar: TIME TO COMPLETE STEPS (MINS.) 16 to TIME TO COMPLETE STEPS (MINS.) 17
MODEL NO. |  | TSS08 | [6 empty] | HTG. MIN. CFM |  |  | --- | [5 empty] | 8 | Balance at calibrated max w/ double check readings. | bar: TIME TO COMPLETE STEPS (MINS.) 18 to TIME TO COMPLETE STEPS (MINS.) 27
SERVICE |  | Conditioned Air | [15 empty] | 9 | Put box to satisfied. | bar: TIME TO COMPLETE STEPS (MINS.) 28 to TIME TO COMPLETE STEPS (MINS.) 29
SERIAL NO. | [17 empty] | 10 | Measure outlets in satisfied condition, record flow. | bar: TIME TO COMPLETE STEPS (MINS.) 30 to TIME TO COMPLETE STEPS (MINS.) 32
DDC TERMINAL # | [17 empty] | 11 | Put box in heat. | bar: TIME TO COMPLETE STEPS (MINS.) 33 to TIME TO COMPLETE STEPS (MINS.) 34
COR. FACTOR | [17 empty] | 12 | Measure outlets and record total. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 2: LEGEND
[18 empty] | 13 | Measure elec. heat components (or water). |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: EIT
[18 empty] | 14 | Measure LAT. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TECH
[18 empty] | 15 | Release the box. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TEAM
[18 empty] | 16 | Make sure all information on the data sheet is filled out.
[21 empty] | PROJECT TOLERANCES | GENERAL FIELD CALC. AREA
ABOVE DESIGN
[17 empty] | FOR PROPORTIONS, CORRECTION FACTORS, ETC. |  |  |  | BELOW DESIGN
AREA SERVED LOCATION |  |  | OUTLETS |  |  |  |  | DESIGN CFM | PRELIMINARY CFM |  |  |  | FINAL CFM |  | REMARKS
|  |  | NO. | TYPE |  |  | SIZE (IN.) |  | TEST1 | TEST 2 |  | TEST 3 | [7 empty] | FINAL CFM TOLERANCE CHECK
Patient Room F117 |  |  | 1 | CSD1 |  |  | 10 | 350
Pat. Tlt. F117A |  |  | 2 | CSD2 |  |  | 6 | 80
TOTAL | [7 empty] | 430
REMARKS
TEST DATE | [7 empty] | READINGS BY

## VAV-PW-05
INTERNAL USE ONLY - DOES NOT PRINT
VARIABLE AIR VOLUME UNIT TEST REPORT
PROJECT | EHC - Tallahassee Reno. & Add. | [7 empty] | SYSTEM |  | RTU-PW01 | [5 empty] | BASIC TESTING WORKFLOW (Indicate Complete with x) | [5 empty] | TIME TO COMPLETE STEPS (MINS.)
[23 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42
AREA SERVED | Patient Room F118 | [7 empty] | LOCATION |  | Corridor F155 | [6 empty] | 1 | Get controls communicating. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
[18 empty] | 2 | Verify duct layout vs drawings with neck size. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
VAV UNIT DATA | [8 empty] | VAV PERFORMANCE DATA | [8 empty] | 3 | Open dampers. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 10
VAV # |  | VAV-PW-05 | [9 empty] | DESIGN |  | ACTUAL |  |  |  | 4 | Put box in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 7
INLET SIZE |  |  |  |  | " | Round |  |  | CLG. MAX. CFM |  |  | 400 | [5 empty] | 5 | Nameplate check against submittal. | bar: TIME TO COMPLETE STEPS (MINS.) 8 to TIME TO COMPLETE STEPS (MINS.) 10
MFG. | [8 empty] | CLG. MIN. CFM |  |  | 240 | [5 empty] | 6 | Measure outlets in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 11 to TIME TO COMPLETE STEPS (MINS.) 15
TYPE |  | VAV | [6 empty] | HTG. MAX. CFM |  |  | 240 | [5 empty] | 7 | Calibrate flow at max. | bar: TIME TO COMPLETE STEPS (MINS.) 16 to TIME TO COMPLETE STEPS (MINS.) 17
MODEL NO. | [8 empty] | HTG. MIN. CFM |  |  | --- | [5 empty] | 8 | Balance at calibrated max w/ double check readings. | bar: TIME TO COMPLETE STEPS (MINS.) 18 to TIME TO COMPLETE STEPS (MINS.) 27
SERVICE |  | Conditioned Air | [15 empty] | 9 | Put box to satisfied. | bar: TIME TO COMPLETE STEPS (MINS.) 28 to TIME TO COMPLETE STEPS (MINS.) 29
SERIAL NO. | [17 empty] | 10 | Measure outlets in satisfied condition, record flow. | bar: TIME TO COMPLETE STEPS (MINS.) 30 to TIME TO COMPLETE STEPS (MINS.) 32
DDC TERMINAL # | [17 empty] | 11 | Put box in heat. | bar: TIME TO COMPLETE STEPS (MINS.) 33 to TIME TO COMPLETE STEPS (MINS.) 34
COR. FACTOR | [17 empty] | 12 | Measure outlets and record total. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 2: LEGEND
[18 empty] | 13 | Measure elec. heat components (or water). |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: EIT
[18 empty] | 14 | Measure LAT. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TECH
[18 empty] | 15 | Release the box. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TEAM
[18 empty] | 16 | Make sure all information on the data sheet is filled out.
[21 empty] | PROJECT TOLERANCES | GENERAL FIELD CALC. AREA
ABOVE DESIGN
[17 empty] | FOR PROPORTIONS, CORRECTION FACTORS, ETC. |  |  |  | BELOW DESIGN
AREA SERVED LOCATION |  |  | OUTLETS |  |  |  |  | DESIGN CFM | PRELIMINARY CFM |  |  |  | FINAL CFM |  | REMARKS
|  |  | NO. | TYPE |  |  | SIZE (IN.) |  | TEST1 | TEST 2 |  | TEST 3 | [7 empty] | FINAL CFM TOLERANCE CHECK
Private F118 |  |  | 1 | CSD1 |  |  | 10 | 300
Corridor F105 |  |  | 2 | " |  |  | 8 | 125
TOTAL | [7 empty] | 425
REMARKS
TEST DATE | [7 empty] | READINGS BY

## VAV-PW-06
INTERNAL USE ONLY - DOES NOT PRINT
VARIABLE AIR VOLUME UNIT TEST REPORT
PROJECT | EHC - Tallahassee Reno. & Add. | [7 empty] | SYSTEM |  | RTU-PW01 | [5 empty] | BASIC TESTING WORKFLOW (Indicate Complete with x) | [5 empty] | TIME TO COMPLETE STEPS (MINS.)
[23 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42
AREA SERVED | Patient Room F119 | [7 empty] | LOCATION |  | Corridor F155 | [6 empty] | 1 | Get controls communicating. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
[18 empty] | 2 | Verify duct layout vs drawings with neck size. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
VAV UNIT DATA | [8 empty] | VAV PERFORMANCE DATA | [8 empty] | 3 | Open dampers. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 10
VAV # |  | VAV-PW-06 | [9 empty] | DESIGN |  | ACTUAL |  |  |  | 4 | Put box in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 7
INLET SIZE |  |  |  |  | " | Round |  |  | CLG. MAX. CFM |  |  | 300 | [5 empty] | 5 | Nameplate check against submittal. | bar: TIME TO COMPLETE STEPS (MINS.) 8 to TIME TO COMPLETE STEPS (MINS.) 10
MFG. | [8 empty] | CLG. MIN. CFM |  |  | 180 | [5 empty] | 6 | Measure outlets in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 11 to TIME TO COMPLETE STEPS (MINS.) 15
TYPE |  | VAV | [6 empty] | HTG. MAX. CFM |  |  | 180 | [5 empty] | 7 | Calibrate flow at max. | bar: TIME TO COMPLETE STEPS (MINS.) 16 to TIME TO COMPLETE STEPS (MINS.) 17
MODEL NO. | [8 empty] | HTG. MIN. CFM |  |  | --- | [5 empty] | 8 | Balance at calibrated max w/ double check readings. | bar: TIME TO COMPLETE STEPS (MINS.) 18 to TIME TO COMPLETE STEPS (MINS.) 27
SERVICE |  | Conditioned Air | [15 empty] | 9 | Put box to satisfied. | bar: TIME TO COMPLETE STEPS (MINS.) 28 to TIME TO COMPLETE STEPS (MINS.) 29
SERIAL NO. | [17 empty] | 10 | Measure outlets in satisfied condition, record flow. | bar: TIME TO COMPLETE STEPS (MINS.) 30 to TIME TO COMPLETE STEPS (MINS.) 32
DDC TERMINAL # | [17 empty] | 11 | Put box in heat. | bar: TIME TO COMPLETE STEPS (MINS.) 33 to TIME TO COMPLETE STEPS (MINS.) 34
COR. FACTOR | [17 empty] | 12 | Measure outlets and record total. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 2: LEGEND
[18 empty] | 13 | Measure elec. heat components (or water). |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: EIT
[18 empty] | 14 | Measure LAT. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TECH
[18 empty] | 15 | Release the box. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TEAM
[18 empty] | 16 | Make sure all information on the data sheet is filled out.
[21 empty] | PROJECT TOLERANCES | GENERAL FIELD CALC. AREA
ABOVE DESIGN
[17 empty] | FOR PROPORTIONS, CORRECTION FACTORS, ETC. |  |  |  | BELOW DESIGN
AREA SERVED LOCATION |  |  | OUTLETS |  |  |  |  | DESIGN CFM | PRELIMINARY CFM |  |  |  | FINAL CFM |  | REMARKS
|  |  | NO. | TYPE |  |  | SIZE (IN.) |  | TEST1 | TEST 2 |  | TEST 3 | [7 empty] | FINAL CFM TOLERANCE CHECK
Private F119 |  |  | 1 | CSD1 |  |  | 10 | 300
TOTAL | [7 empty] | 300
REMARKS
TEST DATE | [7 empty] | READINGS BY

## VAV-PW-13
INTERNAL USE ONLY - DOES NOT PRINT
VARIABLE AIR VOLUME UNIT TEST REPORT
PROJECT | EHC - Tallahassee Reno. & Add. | [7 empty] | SYSTEM |  | RTU-PW01 | [5 empty] | BASIC TESTING WORKFLOW (Indicate Complete with x) | [5 empty] | TIME TO COMPLETE STEPS (MINS.)
[23 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42
AREA SERVED | Private F113 | [7 empty] | LOCATION |  | Corridor F105 | [6 empty] | 1 | Get controls communicating. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
[18 empty] | 2 | Verify duct layout vs drawings with neck size. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
VAV UNIT DATA | [8 empty] | VAV PERFORMANCE DATA | [8 empty] | 3 | Open dampers. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 10
VAV # |  | VAV-PW-13 | [9 empty] | DESIGN |  | ACTUAL |  |  |  | 4 | Put box in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 7
INLET SIZE |  |  |  |  | " | Round |  |  | CLG. MAX. CFM |  |  | 300 | [5 empty] | 5 | Nameplate check against submittal. | bar: TIME TO COMPLETE STEPS (MINS.) 8 to TIME TO COMPLETE STEPS (MINS.) 10
MFG. | [8 empty] | CLG. MIN. CFM |  |  | 180 | [5 empty] | 6 | Measure outlets in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 11 to TIME TO COMPLETE STEPS (MINS.) 15
TYPE |  | VAV | [6 empty] | HTG. MAX. CFM |  |  | 180 | [5 empty] | 7 | Calibrate flow at max. | bar: TIME TO COMPLETE STEPS (MINS.) 16 to TIME TO COMPLETE STEPS (MINS.) 17
MODEL NO. | [8 empty] | HTG. MIN. CFM |  |  | --- | [5 empty] | 8 | Balance at calibrated max w/ double check readings. | bar: TIME TO COMPLETE STEPS (MINS.) 18 to TIME TO COMPLETE STEPS (MINS.) 27
SERVICE |  | Conditioned Air | [15 empty] | 9 | Put box to satisfied. | bar: TIME TO COMPLETE STEPS (MINS.) 28 to TIME TO COMPLETE STEPS (MINS.) 29
SERIAL NO. | [17 empty] | 10 | Measure outlets in satisfied condition, record flow. | bar: TIME TO COMPLETE STEPS (MINS.) 30 to TIME TO COMPLETE STEPS (MINS.) 32
DDC TERMINAL # | [17 empty] | 11 | Put box in heat. | bar: TIME TO COMPLETE STEPS (MINS.) 33 to TIME TO COMPLETE STEPS (MINS.) 34
COR. FACTOR | [17 empty] | 12 | Measure outlets and record total. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 2: LEGEND
[18 empty] | 13 | Measure elec. heat components (or water). |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: EIT
[18 empty] | 14 | Measure LAT. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TECH
[18 empty] | 15 | Release the box. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TEAM
[18 empty] | 16 | Make sure all information on the data sheet is filled out.
[21 empty] | PROJECT TOLERANCES | GENERAL FIELD CALC. AREA
ABOVE DESIGN
[17 empty] | FOR PROPORTIONS, CORRECTION FACTORS, ETC. |  |  |  | BELOW DESIGN
AREA SERVED LOCATION |  |  | OUTLETS |  |  |  |  | DESIGN CFM | PRELIMINARY CFM |  |  |  | FINAL CFM |  | REMARKS
|  |  | NO. | TYPE |  |  | SIZE (IN.) |  | TEST1 | TEST 2 |  | TEST 3 | [7 empty] | FINAL CFM TOLERANCE CHECK
Private F113 |  |  | 1 | CSD1 |  |  | 10 | 300
TOTAL | [7 empty] | 300
REMARKS
TEST DATE | [7 empty] | READINGS BY

## VAV-PW-14
INTERNAL USE ONLY - DOES NOT PRINT
VARIABLE AIR VOLUME UNIT TEST REPORT
PROJECT | EHC - Tallahassee Reno. & Add. | [7 empty] | SYSTEM |  | RTU-PW01 | [5 empty] | BASIC TESTING WORKFLOW (Indicate Complete with x) | [5 empty] | TIME TO COMPLETE STEPS (MINS.)
[23 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42
AREA SERVED | Private F112 | [7 empty] | LOCATION |  | Corridor F105 | [6 empty] | 1 | Get controls communicating. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
[18 empty] | 2 | Verify duct layout vs drawings with neck size. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
VAV UNIT DATA | [8 empty] | VAV PERFORMANCE DATA | [8 empty] | 3 | Open dampers. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 10
VAV # |  | VAV-PW-14 | [9 empty] | DESIGN |  | ACTUAL |  |  |  | 4 | Put box in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 7
INLET SIZE |  |  |  |  | " | Round |  |  | CLG. MAX. CFM |  |  | 350 | [5 empty] | 5 | Nameplate check against submittal. | bar: TIME TO COMPLETE STEPS (MINS.) 8 to TIME TO COMPLETE STEPS (MINS.) 10
MFG. | [8 empty] | CLG. MIN. CFM |  |  | 210 | [5 empty] | 6 | Measure outlets in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 11 to TIME TO COMPLETE STEPS (MINS.) 15
TYPE |  | VAV | [6 empty] | HTG. MAX. CFM |  |  | 210 | [5 empty] | 7 | Calibrate flow at max. | bar: TIME TO COMPLETE STEPS (MINS.) 16 to TIME TO COMPLETE STEPS (MINS.) 17
MODEL NO. | [8 empty] | HTG. MIN. CFM |  |  | --- | [5 empty] | 8 | Balance at calibrated max w/ double check readings. | bar: TIME TO COMPLETE STEPS (MINS.) 18 to TIME TO COMPLETE STEPS (MINS.) 27
SERVICE |  | Conditioned Air | [15 empty] | 9 | Put box to satisfied. | bar: TIME TO COMPLETE STEPS (MINS.) 28 to TIME TO COMPLETE STEPS (MINS.) 29
SERIAL NO. | [17 empty] | 10 | Measure outlets in satisfied condition, record flow. | bar: TIME TO COMPLETE STEPS (MINS.) 30 to TIME TO COMPLETE STEPS (MINS.) 32
DDC TERMINAL # | [17 empty] | 11 | Put box in heat. | bar: TIME TO COMPLETE STEPS (MINS.) 33 to TIME TO COMPLETE STEPS (MINS.) 34
COR. FACTOR | [17 empty] | 12 | Measure outlets and record total. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 2: LEGEND
[18 empty] | 13 | Measure elec. heat components (or water). |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: EIT
[18 empty] | 14 | Measure LAT. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TECH
[18 empty] | 15 | Release the box. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TEAM
[18 empty] | 16 | Make sure all information on the data sheet is filled out.
[21 empty] | PROJECT TOLERANCES | GENERAL FIELD CALC. AREA
ABOVE DESIGN
[17 empty] | FOR PROPORTIONS, CORRECTION FACTORS, ETC. |  |  |  | BELOW DESIGN
AREA SERVED LOCATION |  |  | OUTLETS |  |  |  |  | DESIGN CFM | PRELIMINARY CFM |  |  |  | FINAL CFM |  | REMARKS
|  |  | NO. | TYPE |  |  | SIZE (IN.) |  | TEST1 | TEST 2 |  | TEST 3 | [7 empty] | FINAL CFM TOLERANCE CHECK
Private F112 |  |  | 1 | CSD1 |  |  | 10 | 300
Corridor F105 |  |  | 2 | " |  |  | 6 | 50
TOTAL | [7 empty] | 350
REMARKS
TEST DATE | [7 empty] | READINGS BY

## VAV-PW-15
INTERNAL USE ONLY - DOES NOT PRINT
VARIABLE AIR VOLUME UNIT TEST REPORT
PROJECT | EHC - Tallahassee Reno. & Add. | [7 empty] | SYSTEM |  | RTU-PW01 | [5 empty] | BASIC TESTING WORKFLOW (Indicate Complete with x) | [5 empty] | TIME TO COMPLETE STEPS (MINS.)
[23 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42
AREA SERVED | Private F154 | [7 empty] | LOCATION |  | Corridor F105 | [6 empty] | 1 | Get controls communicating. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
[18 empty] | 2 | Verify duct layout vs drawings with neck size. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
VAV UNIT DATA | [8 empty] | VAV PERFORMANCE DATA | [8 empty] | 3 | Open dampers. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 10
VAV # |  | VAV-PW-15 | [9 empty] | DESIGN |  | ACTUAL |  |  |  | 4 | Put box in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 7
INLET SIZE |  |  |  |  | " | Round |  |  | CLG. MAX. CFM |  |  | 300 | [5 empty] | 5 | Nameplate check against submittal. | bar: TIME TO COMPLETE STEPS (MINS.) 8 to TIME TO COMPLETE STEPS (MINS.) 10
MFG. | [8 empty] | CLG. MIN. CFM |  |  | 180 | [5 empty] | 6 | Measure outlets in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 11 to TIME TO COMPLETE STEPS (MINS.) 15
TYPE |  | VAV | [6 empty] | HTG. MAX. CFM |  |  | 180 | [5 empty] | 7 | Calibrate flow at max. | bar: TIME TO COMPLETE STEPS (MINS.) 16 to TIME TO COMPLETE STEPS (MINS.) 17
MODEL NO. | [8 empty] | HTG. MIN. CFM |  |  | --- | [5 empty] | 8 | Balance at calibrated max w/ double check readings. | bar: TIME TO COMPLETE STEPS (MINS.) 18 to TIME TO COMPLETE STEPS (MINS.) 27
SERVICE |  | Conditioned Air | [15 empty] | 9 | Put box to satisfied. | bar: TIME TO COMPLETE STEPS (MINS.) 28 to TIME TO COMPLETE STEPS (MINS.) 29
SERIAL NO. | [17 empty] | 10 | Measure outlets in satisfied condition, record flow. | bar: TIME TO COMPLETE STEPS (MINS.) 30 to TIME TO COMPLETE STEPS (MINS.) 32
DDC TERMINAL # | [17 empty] | 11 | Put box in heat. | bar: TIME TO COMPLETE STEPS (MINS.) 33 to TIME TO COMPLETE STEPS (MINS.) 34
COR. FACTOR | [17 empty] | 12 | Measure outlets and record total. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 2: LEGEND
[18 empty] | 13 | Measure elec. heat components (or water). |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: EIT
[18 empty] | 14 | Measure LAT. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TECH
[18 empty] | 15 | Release the box. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TEAM
[18 empty] | 16 | Make sure all information on the data sheet is filled out.
[21 empty] | PROJECT TOLERANCES | GENERAL FIELD CALC. AREA
ABOVE DESIGN
[17 empty] | FOR PROPORTIONS, CORRECTION FACTORS, ETC. |  |  |  | BELOW DESIGN
AREA SERVED LOCATION |  |  | OUTLETS |  |  |  |  | DESIGN CFM | PRELIMINARY CFM |  |  |  | FINAL CFM |  | REMARKS
|  |  | NO. | TYPE |  |  | SIZE (IN.) |  | TEST1 | TEST 2 |  | TEST 3 | [7 empty] | FINAL CFM TOLERANCE CHECK
Private F154 |  |  | 1 | CSD1 |  |  | 10 | 300
TOTAL | [7 empty] | 300
REMARKS
TEST DATE | [7 empty] | READINGS BY

## VAV-PW-22
INTERNAL USE ONLY - DOES NOT PRINT
VARIABLE AIR VOLUME UNIT TEST REPORT
PROJECT | EHC - Tallahassee Reno. & Add. | [7 empty] | SYSTEM |  | RTU-PW01 | [5 empty] | BASIC TESTING WORKFLOW (Indicate Complete with x) | [5 empty] | TIME TO COMPLETE STEPS (MINS.)
[23 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42
AREA SERVED | Elec. F104A | [7 empty] | LOCATION |  | Nurse Work F103 | [6 empty] | 1 | Get controls communicating. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
[18 empty] | 2 | Verify duct layout vs drawings with neck size. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
VAV UNIT DATA | [8 empty] | VAV PERFORMANCE DATA | [8 empty] | 3 | Open dampers. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 10
VAV # |  | VAV-PW-22 | [9 empty] | DESIGN |  | ACTUAL |  |  |  | 4 | Put box in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 7
INLET SIZE |  | 6 |  |  | " | Round |  |  | CLG. MAX. CFM |  |  | 100 | [5 empty] | 5 | Nameplate check against submittal. | bar: TIME TO COMPLETE STEPS (MINS.) 8 to TIME TO COMPLETE STEPS (MINS.) 10
MFG. |  | JCI | [6 empty] | CLG. MIN. CFM |  |  | 60 | [5 empty] | 6 | Measure outlets in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 11 to TIME TO COMPLETE STEPS (MINS.) 15
TYPE |  | VAV | [6 empty] | HTG. MAX. CFM |  |  | --- | [5 empty] | 7 | Calibrate flow at max. | bar: TIME TO COMPLETE STEPS (MINS.) 16 to TIME TO COMPLETE STEPS (MINS.) 17
MODEL NO. |  | TSS06 | [6 empty] | HTG. MIN. CFM |  |  | --- | [5 empty] | 8 | Balance at calibrated max w/ double check readings. | bar: TIME TO COMPLETE STEPS (MINS.) 18 to TIME TO COMPLETE STEPS (MINS.) 27
SERVICE |  | Conditioned Air | [15 empty] | 9 | Put box to satisfied. | bar: TIME TO COMPLETE STEPS (MINS.) 28 to TIME TO COMPLETE STEPS (MINS.) 29
SERIAL NO. | [17 empty] | 10 | Measure outlets in satisfied condition, record flow. | bar: TIME TO COMPLETE STEPS (MINS.) 30 to TIME TO COMPLETE STEPS (MINS.) 32
DDC TERMINAL # | [17 empty] | 11 | Put box in heat. | bar: TIME TO COMPLETE STEPS (MINS.) 33 to TIME TO COMPLETE STEPS (MINS.) 34
COR. FACTOR | [17 empty] | 12 | Measure outlets and record total. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 2: LEGEND
[18 empty] | 13 | Measure elec. heat components (or water). |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: EIT
[18 empty] | 14 | Measure LAT. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TECH
[18 empty] | 15 | Release the box. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TEAM
[18 empty] | 16 | Make sure all information on the data sheet is filled out.
[21 empty] | PROJECT TOLERANCES | GENERAL FIELD CALC. AREA
ABOVE DESIGN
[17 empty] | FOR PROPORTIONS, CORRECTION FACTORS, ETC. |  |  |  | BELOW DESIGN
AREA SERVED LOCATION |  |  | OUTLETS |  |  |  |  | DESIGN CFM | PRELIMINARY CFM |  |  |  | FINAL CFM |  | REMARKS
|  |  | NO. | TYPE |  |  | SIZE (IN.) |  | TEST1 | TEST 2 |  | TEST 3 | [7 empty] | FINAL CFM TOLERANCE CHECK
Elec. F104A |  |  | 1 | WSG1 |  |  | 9x9 | 100
TOTAL | [7 empty] | 100
REMARKS
TEST DATE | [7 empty] | READINGS BY

## VAV-PW-23
INTERNAL USE ONLY - DOES NOT PRINT
VARIABLE AIR VOLUME UNIT TEST REPORT
PROJECT | EHC - Tallahassee Reno. & Add. | [7 empty] | SYSTEM |  | RTU-PW01 | [5 empty] | BASIC TESTING WORKFLOW (Indicate Complete with x) | [5 empty] | TIME TO COMPLETE STEPS (MINS.)
[23 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42
AREA SERVED | Nurse Work F103 | [7 empty] | LOCATION |  | Nurse Work F103 | [6 empty] | 1 | Get controls communicating. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
[18 empty] | 2 | Verify duct layout vs drawings with neck size. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
VAV UNIT DATA | [8 empty] | VAV PERFORMANCE DATA | [8 empty] | 3 | Open dampers. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 10
VAV # |  | VAV-PW-23 | [9 empty] | DESIGN |  | ACTUAL |  |  |  | 4 | Put box in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 7
INLET SIZE |  | 6 |  |  | " | Round |  |  | CLG. MAX. CFM |  |  | 325 | [5 empty] | 5 | Nameplate check against submittal. | bar: TIME TO COMPLETE STEPS (MINS.) 8 to TIME TO COMPLETE STEPS (MINS.) 10
MFG. |  | JCI | [6 empty] | CLG. MIN. CFM |  |  | 200 | [5 empty] | 6 | Measure outlets in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 11 to TIME TO COMPLETE STEPS (MINS.) 15
TYPE |  | VAV | [6 empty] | HTG. MAX. CFM |  |  | 200 | [5 empty] | 7 | Calibrate flow at max. | bar: TIME TO COMPLETE STEPS (MINS.) 16 to TIME TO COMPLETE STEPS (MINS.) 17
MODEL NO. |  | TSS06 | [6 empty] | HTG. MIN. CFM |  |  | --- | [5 empty] | 8 | Balance at calibrated max w/ double check readings. | bar: TIME TO COMPLETE STEPS (MINS.) 18 to TIME TO COMPLETE STEPS (MINS.) 27
SERVICE |  | Conditioned Air | [15 empty] | 9 | Put box to satisfied. | bar: TIME TO COMPLETE STEPS (MINS.) 28 to TIME TO COMPLETE STEPS (MINS.) 29
SERIAL NO. | [17 empty] | 10 | Measure outlets in satisfied condition, record flow. | bar: TIME TO COMPLETE STEPS (MINS.) 30 to TIME TO COMPLETE STEPS (MINS.) 32
DDC TERMINAL # | [17 empty] | 11 | Put box in heat. | bar: TIME TO COMPLETE STEPS (MINS.) 33 to TIME TO COMPLETE STEPS (MINS.) 34
COR. FACTOR | [17 empty] | 12 | Measure outlets and record total. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 2: LEGEND
[18 empty] | 13 | Measure elec. heat components (or water). |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: EIT
[18 empty] | 14 | Measure LAT. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TECH
[18 empty] | 15 | Release the box. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TEAM
[18 empty] | 16 | Make sure all information on the data sheet is filled out.
[21 empty] | PROJECT TOLERANCES | GENERAL FIELD CALC. AREA
ABOVE DESIGN
[17 empty] | FOR PROPORTIONS, CORRECTION FACTORS, ETC. |  |  |  | BELOW DESIGN
AREA SERVED LOCATION |  |  | OUTLETS |  |  |  |  | DESIGN CFM | PRELIMINARY CFM |  |  |  | FINAL CFM |  | REMARKS
|  |  | NO. | TYPE |  |  | SIZE (IN.) |  | TEST1 | TEST 2 |  | TEST 3 | [7 empty] | FINAL CFM TOLERANCE CHECK
Nurse Work F103 |  |  | 1 | CSD1 |  |  | 6 | 25
" |  |  | 2 | " |  |  | " | 100
" |  |  | 3 | " |  |  | 8 | 200
TOTAL | [7 empty] | 325
REMARKS
TEST DATE | [7 empty] | READINGS BY

## VAV-PW-24
INTERNAL USE ONLY - DOES NOT PRINT
VARIABLE AIR VOLUME UNIT TEST REPORT
PROJECT | EHC - Tallahassee Reno. & Add. | [7 empty] | SYSTEM |  | RTU-PW01 | [5 empty] | BASIC TESTING WORKFLOW (Indicate Complete with x) | [5 empty] | TIME TO COMPLETE STEPS (MINS.)
[23 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42
AREA SERVED | Clean Hold F101 | [7 empty] | LOCATION |  | Clean Hold F101 | [6 empty] | 1 | Get controls communicating. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
[18 empty] | 2 | Verify duct layout vs drawings with neck size. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
VAV UNIT DATA | [8 empty] | VAV PERFORMANCE DATA | [8 empty] | 3 | Open dampers. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 10
VAV # |  | VAV-PW-24 | [9 empty] | DESIGN |  | ACTUAL |  |  |  | 4 | Put box in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 7
INLET SIZE |  | 6 |  |  | " | Round |  |  | CLG. MAX. CFM |  |  | 200 | [5 empty] | 5 | Nameplate check against submittal. | bar: TIME TO COMPLETE STEPS (MINS.) 8 to TIME TO COMPLETE STEPS (MINS.) 10
MFG. |  | JCI | [6 empty] | CLG. MIN. CFM |  |  | 120 | [5 empty] | 6 | Measure outlets in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 11 to TIME TO COMPLETE STEPS (MINS.) 15
TYPE |  | VAV | [6 empty] | HTG. MAX. CFM |  |  | 120 | [5 empty] | 7 | Calibrate flow at max. | bar: TIME TO COMPLETE STEPS (MINS.) 16 to TIME TO COMPLETE STEPS (MINS.) 17
MODEL NO. |  | TSS06 | [6 empty] | HTG. MIN. CFM |  |  | --- | [5 empty] | 8 | Balance at calibrated max w/ double check readings. | bar: TIME TO COMPLETE STEPS (MINS.) 18 to TIME TO COMPLETE STEPS (MINS.) 27
SERVICE |  | Conditioned Air | [15 empty] | 9 | Put box to satisfied. | bar: TIME TO COMPLETE STEPS (MINS.) 28 to TIME TO COMPLETE STEPS (MINS.) 29
SERIAL NO. | [17 empty] | 10 | Measure outlets in satisfied condition, record flow. | bar: TIME TO COMPLETE STEPS (MINS.) 30 to TIME TO COMPLETE STEPS (MINS.) 32
DDC TERMINAL # | [17 empty] | 11 | Put box in heat. | bar: TIME TO COMPLETE STEPS (MINS.) 33 to TIME TO COMPLETE STEPS (MINS.) 34
COR. FACTOR | [17 empty] | 12 | Measure outlets and record total. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 2: LEGEND
[18 empty] | 13 | Measure elec. heat components (or water). |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: EIT
[18 empty] | 14 | Measure LAT. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TECH
[18 empty] | 15 | Release the box. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TEAM
[18 empty] | 16 | Make sure all information on the data sheet is filled out.
[21 empty] | PROJECT TOLERANCES | GENERAL FIELD CALC. AREA
ABOVE DESIGN
[17 empty] | FOR PROPORTIONS, CORRECTION FACTORS, ETC. |  |  |  | BELOW DESIGN
AREA SERVED LOCATION |  |  | OUTLETS |  |  |  |  | DESIGN CFM | PRELIMINARY CFM |  |  |  | FINAL CFM |  | REMARKS
|  |  | NO. | TYPE |  |  | SIZE (IN.) |  | TEST1 | TEST 2 |  | TEST 3 | [7 empty] | FINAL CFM TOLERANCE CHECK
Clean Hold F101 |  |  | 1 | CSD1 |  |  | 8 | 200
TOTAL | [7 empty] | 200
REMARKS
TEST DATE | [7 empty] | READINGS BY