## FCUFLYER
Fan Coil Unit Systems Test Reports

## FCU-1
INTERNAL USE ONLY - DOES NOT PRINT
GENERAL FIELD CALC. AREA
FAN COIL UNIT TEST REPORT
PROJECT |  |  | EHC - Tallahassee Reno. & Add. | [9 empty] | SYSTEM |  | FCU-1
AREA SERVED |  |  | Comm F109 | [9 empty] | LOCATION |  | Comm F109
UNIT DATA | [12 empty] | FILTER DATA | [8 empty] | MOTOR ACTUAL BHP CALCS.
MFG. |  |  |  | York | [8 empty] | FILTER SECTION | [9 empty] | AMPS. | VOLTS |  |  |  |  | AMP IMBALANCE TEST1 |  | VOLT IMBALANCE TEST2
TYPE |  |  |  | HDT | [8 empty] | QUANTITY | [8 empty] | TEST 1 |  |  | MOTOR EFF.
MODEL NO. |  |  |  | DHX24NWB21S | [8 empty] | SIZE (in.) | [8 empty] | TEST 2
SERVICE |  |  |  | Conditioned Air | [8 empty] | TYPE | [8 empty] | TEST 3 |  |  | POWER FACTOR
SERIAL NO. | [12 empty] | S.P. ACROSS |  |  |  | "w.c. |  |  | "w.c. |  | AVG. | [6 empty] | 1. Amp imbalance may indicate problems with the motor or power supply.
[13 empty] | CONDITION | [11 empty] | MOTOR PHASE |  |  |  | 2. Volt imbalance may cause motors to overheat. Many solid-state motor controllers and inverters are sensitive to imbalanced voltage.
SUPPLY FAN DATA
|  | CFM |  | TSP |  | ESP |  | RPM |  | BHP |  | ROTATION | [9 empty] | POWER TRANSMISSION (PT) CALCS. | [7 empty] | DETERMINING FAN ROTATION
DESIGN |  | 706 |  | --- |  | --- |  | --- |  | --- | [11 empty] | MTR TO FAN SHEAVE RATIO
ACTUAL | [21 empty] | CALC. BELT LENGTH |  |  |  |  | "
FAN MOTOR RPM PER PT
AIRFLOW DATA | [11 empty] | POWER TRANSMISSION DATA |  |  |  |  | X |  |  |  |  | MIN. FAN MTR RPM PER PT1
|  |  |  | RETURN |  |  | OUTSIDE |  |  |  |  | TRANSMISSION TYPE | [9 empty] | 1. If fan motor RPM falls below this min. number (cell red) check for belt slippage or belt riding on motor shaft. Based on 0.5" reduction on motor and fan sheave.
DESIGN (CFM) |  |  |  | 706 |  |  | 0 |  |  |  |  | MOTOR SHEAVE MFG.
ACTUAL (CFM) | [11 empty] | MOTOR SHEAVE |  |  |  |  | "I.D. |  |  | "O.D.
DAMPER POS. | [5 empty] | Open |  |  | Open |  |  | FAN SHEAVE MFG.
[12 empty] | FAN SHEAVE |  |  |  |  | "I.D. |  |  | "O.D.
MOTOR DATA |  |  | X | [8 empty] | BELT MFG.
MFG. | [11 empty] | NO. BELTS & SIZE | [5 empty] | @
FRAME | [11 empty] | CENTER DISTANCE | [6 empty] | "C.C.
H.P. | [21 empty] | DUCT DP SETPOINT CALC. (+20% Tol.)
SERVICE FACTOR | [15 empty] | DUCT STATIC PRESSURE
[5 empty] | DESIGN |  |  | ACTUAL | [7 empty] | SETPOINT |  |  |  | "w.c.
RPM | [15 empty] | ACT. MEASUREMENT |  |  |  | "w.c.
FULL LOAD AMPS. | [7 empty] | ---
CRT. NAME AMPS. |  |  |  |  | ---
OP. AMPS. |  |  |  |  | --- | [8 empty] | SUPPLY FAN SPEED FINAL SETTING | [7 empty] | STATIC PRESSURE PROFILE SELECTIONS |  |  |  | BASIC TESTING WORKFLOW (Indicate Complete with x)
VOLTS | [26 empty] | 1
[22 empty] | A - B |  |  |  |  | 2 | Verify duct layout (areas served) vs drawings and neck sizes.
STATIC PRESSURE PROFILE "w.c. | [21 empty] | B - C |  |  |  |  | 3 | Check nameplate against submittal.
COMPONENT | [21 empty] | C - D |  |  |  |  | 4 | Open dampers and check that automatic dampers open when the system is energized.
[22 empty] | D - E |  |  |  |  | 5 | Check pulley alignment and tightness.
[22 empty] | E - F |  |  |  |  | 6 | Put the unit into full cooling.
[22 empty] | F - G |  |  |  |  | 7 | Check rotation.
PRESSURE | [21 empty] | G - H |  |  |  |  | 8 | Measure the inlets / outlets on the system.
[22 empty] | H - I |  |  |  |  | 9 | Proportion the inlets / outlets to the available airflow.
[22 empty] | I - J |  |  |  |  | 10 | Adjust rpm as needed to achieve design airflow based on rpm vs cfm equation.
| REMARKS | [20 empty] | J - K |  |  |  |  | 11 | Adjust outside and return air to design.
[27 empty] | 12 | Measure rpm, amperage and voltage.
[27 empty] | 13 | Measure inlets / outlets on the system.
[27 empty] | 14 | Record unit pressure profile (before filter, after filter, suction and discharge pressures etc.)
[27 empty] | 15 | Measure the entering and leaving chilled water pressure and set to design if applicable.
[27 empty] | 16 | Measure the entering and leaving dry and wet bulb temperatures across the cooling coil.
[27 empty] | 17 | Put the unit into full heating if applicable.
[27 empty] | 18 | Measure the total airflow and record differences to design.
[27 empty] | 19 | Measure electric heating components or heating hot water pressures and set to design.
[27 empty] | 20 | Measure entering and leaving air temperature (dry bulb only).
[26 empty] | Note - Measure total supply, return and outside airflows by traverse when possible. |  | Make sure all information on the data sheet is filled out.
TEST DATE | [10 empty] | READINGS BY
LOOKING
CCW

## FCU-1 - SUPTRAV-VEL
INTERNAL USE ONLY - DOES NOT PRINT
SUPPLY AIR TRAVERSE TEST REPORT
PROJECT |  |  |  | EHC - Tallahassee Reno. & Add. | [15 empty] | SYSTEM |  |  | FCU-1
PROJECT TOLERANCES
AREA SERVED |  |  |  | Comm F109 | [15 empty] | LOCATION |  |  | Comm F109 | [6 empty] | ABOVE DESIGN
BELOW DESIGN
TRAVERSE DATA
TRAVERSE AREA | [9 empty] | DESIGN AIRFLOW | [9 empty] | ACTUAL AIRFLOW | [8 empty] | FINAL CFM TOLERANCE CHECK
SIZE |  | "W |  |  | "H |  | SQ. FT. |  |  | FPM |  |  |  | CFM |  | 706 |  |  |  | FPM |  |  |  |  | CFM
[12 empty] | OP. FREQ. FINAL SETTING | [7 empty] | TESTING EQUIPMENT
[20 empty] | INSTRUMENT |  |  | Air Data Multimeter - Velocity Grid
AIR VELOCITY READINGS (FPM) | [28 empty] | (W) WIDTH DISTANCE AND NO. OF POINT CALCS.
POSITION (IN.) |  |  |  |  | 1 | 2 |  | 3 | 4 |  | 5 |  | 6 | 7 |  | 8 |  | 9 |  |  | 10 | 11 |  | 12 |  | 13 | 14
NO. |  |  | POINT |  | 6 | [23 empty] | WIDTH "
1 |  |  | 6 | [25 empty] | NO. OF POINTS
2 | [28 empty] | POINT DISTANCE " | [5 empty] | GENERAL FIELD CALC. AREA
3
4 | [28 empty] | (H) HEIGHT DISTANCE AND NO. OF POINT CALCS.
5
6 | [28 empty] | HEIGHT "
7 | [28 empty] | NO. OF POINTS
8 | [28 empty] | POINT DISTANCE "
9
10 | [28 empty] | DECIMAL TO FRACTION CONVERTER (Fraction as Quarters)
SUB-TOTAL |  |  |  |  | 0 | [23 empty] | POSITION |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
[29 empty] | NO. |  | POINT | 6
| REMARKS | [17 empty] | CENTERLINE TRAVERSE SP | [7 empty] | "w.c. |  | 1 |  | 6
[19 empty] | AIR TEMPERATURE | [7 empty] | °F |  | 2
[19 empty] | TOTAL READINGS | [7 empty] | FPM |  | 3
[19 empty] | NO. READINGS | [9 empty] | 4
[19 empty] | AVG. VELOCITY | [7 empty] | FPM |  | 5
[19 empty] | EFFECTIVE AREA MULTIPLIER | [9 empty] | 6
[19 empty] | AREA | [7 empty] | SQ. FT. |  | 7
[19 empty] | TOTAL AIRFLOW | [7 empty] | CFM |  | 8
9
TEST DATE | [16 empty] | READINGS BY | [11 empty] | 10

## FCU-1 - SUPTRAV-PTO
INTERNAL USE ONLY - DOES NOT PRINT
SUPPLY AIR TRAVERSE TEST REPORT
PROJECT |  |  |  | EHC - Tallahassee Reno. & Add. | [17 empty] | SYSTEM |  |  | FCU-1
[34 empty] | PROJECT TOLERANCES | DECIMAL TO FRACTION CONVERTER (Fraction as Quarters)
AREA SERVED |  |  |  | Comm F109 | [17 empty] | LOCATION |  |  | Comm F109 | [8 empty] | ABOVE DESIGN | POSITION (IN.) |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
[34 empty] | BELOW DESIGN | NO. | POINT
TRAVERSE DATA | [34 empty] | 1
DUCT SIZE | [9 empty] | DESIGN AIRFLOW | [11 empty] | ACTUAL AIRFLOW | [10 empty] | FINAL CFM TOLERANCE CHECK |  | 2
"W |  |  | PORT # |  |  |  | SQ. FT. |  |  | FPM |  |  |  | CFM |  |  | 706 |  |  |  |  | FPM |  |  |  |  | CFM | [7 empty] | 3
"H |  |  | PORT # | [31 empty] | 4
[8 empty] | OP. FREQ. FINAL SETTING | [6 empty] | TESTING EQUIPMENT INSTRUMENT | [9 empty] | Air Data Multimeter - Pitot Tube | [7 empty] | (W) WIDTH DISTANCE AND NO. OF POINT CALCS. |  | 5
6
AIR VELOCITY READINGS (FPM) | [32 empty] | WIDTH " |  | 7
POSITION (IN.) | [32 empty] | NO. OF POINTS |  | 8
NO. |  | POINT | VP |  | VEL | VP | VEL | VP | VEL | VP | VEL | VP | VEL | VP |  | VEL |  | VP |  | VEL |  | VP | VEL | VP |  | VEL | VP | VEL | VP |  | VEL |  | POINT DISTANCE " |  | 9
1 | [34 empty] | 10
2 | [32 empty] | (H) HEIGHT DISTANCE AND NO. OF POINT CALCS.
3
4 | [32 empty] | HEIGHT "
5 | [32 empty] | NO. OF POINTS
6 | [32 empty] | POINT DISTANCE "
7
8 | [32 empty] | GENERAL FIELD CALC. AREA
9
10
SUB-TOTAL
REMARKS
[21 empty] | CENTERLINE TRAVERSE ("w.c.) | [6 empty] | TP |  | SP
[21 empty] | AIR TEMPERATURE | [8 empty] | °F
[21 empty] | TOTAL READINGS | [8 empty] | FPM |  |  | If you have a VP that is 0.00 you need to unlock the sheet and adjust ALL VP
NO. READINGS
[21 empty] | AVG. VELOCITY | [8 empty] | FPM |  |  | columns to the thousandth decimal place and re-enter the traverse with three digits.
EFFECTIVE AREA MULTIPLIER
[21 empty] | AREA | [8 empty] | SQ. FT. |  |  | In most cases a 0.00 will move to a 0.002 or a 0.001 etc. A legitimate zero VP (0.00 or 0.000) is a
[21 empty] | TOTAL AIRFLOW | [8 empty] | CFM |  |  | red flag in report reviews. Note: Do not adjust the decimal place for the "VEL" columns.
TEST DATE | [18 empty] | READINGS BY

## FCU-1 - SUPTRAV-RNDPTO
INTERNAL USE ONLY - DOES NOT PRINT
SUPPLY AIR TRAVERSE TEST REPORT
PROJECT |  |  |  | EHC - Tallahassee Reno. & Add. | [13 empty] | SYSTEM | FCU-1
PROJECT TOLERANCES
AREA SERVED |  |  |  | Comm F109 | [13 empty] | LOCATION | Comm F109 | [5 empty] | ABOVE DESIGN
BELOW DESIGN
TRAVERSE DATA
TRAVERSE AREA | [10 empty] | DESIGN AIRFLOW | [6 empty] | ACTUAL AIRFLOW | [5 empty] | FINAL CFM TOLERANCE CHECK
SIZE |  |  | " ROUND |  |  | SQ. FT. |  | 0 |  |  | FPM |  | CFM |  | 706 |  |  | FPM |  | CFM
AIR VELOCITY READINGS (FPM) | [11 empty] | OP. FREQ. FINAL SETTING | [5 empty] | TESTING EQUIPMENT | [5 empty] | GENERAL FIELD CALC. AREA
POSITION |  |  |  |  | X AXIS |  |  |  | Y AXIS | [8 empty] | INSTRUMENT | Air Data Multimeter - Pitot Tube
NO. |  | POINT |  |  | VP |  | VEL |  | VP | VEL
1 |  | 0
2 |  | 0
3 |  | 0
4 |  | 0
5 |  | 0
6 |  | 0
7 |  | 0
8 |  | 0
9 |  | 0
10 |  | 0
SUB-TOTAL |  |  |  |  | --- |  |  |  | ---
| REMARKS | [15 empty] | CENTERLINE TRAVERSE SP |  |  |  |  | "w.c. |  | If you have a VP that is 0.00 you need to unlock the sheet and adjust ALL VP
[17 empty] | AIR TEMPERATURE |  |  |  |  | °F
[17 empty] | TOTAL READINGS |  |  |  | 0 | FPM |  | columns to the thousandth decimal place and re-enter the traverse with three digits.
[17 empty] | NO. READINGS |  |  |  | 0
[17 empty] | AVG. VELOCITY |  |  |  |  | FPM |  | In most cases a 0.00 will move to a 0.002 or a 0.001 etc. A legitimate zero VP (0.00 or 0.000) is a
[17 empty] | EFFECTIVE AREA MULTIPLIER | [6 empty] | red flag in report reviews. Note: Do not adjust the decimal place for the "VEL" columns.
[17 empty] | AREA |  |  |  | 0 | SQ. FT.
[17 empty] | TOTAL AIRFLOW |  |  |  |  | CFM
TEST DATE | [15 empty] | READINGS BY
X AXIS
Y AXIS

## FCU-1 - OUTLETSUM-1
INTERNAL USE ONLY - DOES NOT PRINT
OUTLET TEST REPORT
PROJECT |  | EHC - Tallahassee Reno. & Add. | [5 empty] | SYSTEM |  | FCU-1
PROJECT TOLERANCES
[17 empty] | ABOVE DESIGN | GENERAL FIELD CALC. AREA
[15 empty] | FOR PROPORTIONS, CORRECTION FACTORS, ETC. |  | BELOW DESIGN
AREA SERVED LOCATION |  |  | OUTLETS |  |  |  | DESIGN CFM | PRELIMINARY CFM |  |  |  | FINAL CFM | REMARKS
|  |  | NO. | TYPE |  | SIZE (IN.) |  | TEST1 | TEST 2 |  | TEST 3 |  |  |  |  | FINAL CFM TOLERANCE CHECK
Comm F109 |  |  | 1 | --- |  |  | 706
TOTAL | [6 empty] | 706
706
REMARKS
TEST DATE | [6 empty] | READINGS BY