## EF-PW-04
INTERNAL USE ONLY - DOES NOT PRINT
FAN TEST REPORT
PROJECT |  | EHC - Tallahassee Reno. & Add. | [10 empty] | SYSTEM |  |  | EF-PW-04
AREA SERVED |  | Patient Toilets | [10 empty] | LOCATION |  |  | Roof
UNIT DATA | [11 empty] | MOTOR DATA | [10 empty] | FAN MOTOR ACTUAL BHP CALCS.
MFG. | [11 empty] | MFG. | [11 empty] | AMPS. | VOLTS |  |  |  |  | AMP IMBALANCE TEST1 |  | VOLT IMBALANCE TEST2
TYPE | [11 empty] | FRAME | [10 empty] | TEST 1 |  |  | MOTOR EFF.
MODEL NO. | [11 empty] | H.P. | [10 empty] | TEST 2
SERVICE |  |  | Ventilation | [8 empty] | SERVICE FACTOR | [10 empty] | TEST 3 |  |  | POWER FACTOR
SERIAL NO. | [16 empty] | DESIGN |  | ACTUAL |  |  |  | AVG. | [6 empty] | 1. Amp imbalance may indicate problems with the motor or power supply.
[12 empty] | RPM | [13 empty] | MOTOR PHASE |  |  |  | 2. Volt imbalance may cause motors to overheat. Many solid-state motor controllers and inverters are sensitive to imbalanced voltage.
POWER TRANSMISSION DATA | [11 empty] | FULL LOAD AMPS.
TRANSMISSION TYPE | [11 empty] | CRT. NAME AMPS. |  |  |  |  | ---
MOTOR SHEAVE MFG. | [11 empty] | OP. AMPS. |  |  |  |  | --- | [5 empty] | POWER TRANSMISSION (PT) CALCS. | [7 empty] | DETERMINING FAN ROTATION
MOTOR SHEAVE | [5 empty] | "I.D. |  |  |  | "O.D. |  | VOLTS | [10 empty] | MTR TO FAN SHEAVE RATIO
FAN SHEAVE MFG. | [22 empty] | CALC. BELT LENGTH | [5 empty] | "
FAN SHEAVE | [5 empty] | "I.D. |  |  |  | "O.D. |  |  |  |  | FAN FINAL SETTINGS | [7 empty] | FAN MOTOR RPM PER PT |  |  | #VALUE!
BELT MFG. | [22 empty] | MIN. FAN MTR RPM PER PT1 |  |  | #VALUE!
NO. BELTS & SIZE | [6 empty] | @ | [7 empty] | FAN DISCHARGE | [5 empty] | + "w.c. |  | 1. If fan motor RPM falls below this min. number (cell red) check for belt slippage or belt riding on motor shaft. Based on 0.5" reduction on motor and fan sheave.
CENTER DISTANCE | [7 empty] | "C.C. | [6 empty] | FAN SUCTION | [5 empty] | - "w.c.
FAN DATA
| CFM |  | TSP |  | ESP |  |  | RPM |  | BHP |  | ROTATION
DESIGN | [27 empty] | PROJECT TOLERANCES
ACTUAL |  |  | 0 | [24 empty] | ABOVE DESIGN
[23 empty] | FOR PROPORTIONS, CORRECTION FACTORS, ETC. |  |  |  |  | BELOW DESIGN
AREA SERVED LOCATION |  |  |  | INLETS | [6 empty] | DESIGN CFM |  | PRELIMINARY CFM |  |  |  |  | FINAL CFM |  | REMARKS
|  |  |  | NO. |  | TYPE |  |  | SIZE (IN.) |  |  |  | TEST1 | TEST 2 |  |  | TEST 3 | [9 empty] | FINAL CFM TOLERANCE CHECK
Pat. Tlt. F154A |  |  |  | 1 |  | CEG1 |  |  | 6 |  | 75
Pat. Tlt. F153A |  |  |  | 2 |  | " |  |  | " |  | 75
Pat. Tlt. F152A |  |  |  | 3 |  | " |  |  | " |  | 75 | [19 empty] | BASIC TESTING WORKFLOW (Indicate Complete with x)
Soiled Work F151 |  |  |  | 4 |  | CEG2 |  |  | 10 |  | 200 | [20 empty] | 1 | Verify duct layout (areas served) vs drawings with neck sizes.
[32 empty] | 2 | Nameplate check against submitttal.
[32 empty] | 3 | Open dampers and verify gravity and / or automatic dampers open when the system is engerized.
[32 empty] | 4 | Check pulley alignment and tightness.
[32 empty] | 5 | Check rotation.
[32 empty] | 6 | Measure initial amperage and rpm.
[32 empty] | 7 | Set rpm to 10% high if amps will allow, lower rpm if needed based on amperage.
[32 empty] | 8 | Measure the inlets / outlets on the system.
[32 empty] | 9 | Proportion the inlets / outlets to the available airflow.
[32 empty] | 10 | Adjust rpm as needed to achieve design airflow based on rpm vs cfm equation.
[32 empty] | 11 | Measure rpm, amperage and voltage.
[32 empty] | 12 | Measure inlets / outlets on the system.
[32 empty] | 13 | Record suction and discharge pressures.
[32 empty] | 14 | Make sure all information on the data sheet is filled out.
TOTAL | [10 empty] | 425
REMARKS | [26 empty] | GENERAL FIELD CALC. AREA
TEST DATE | [10 empty] | READINGS BY
LOOKING
CCW

## EF-PW-04 - EXHTRAV-VEL
INTERNAL USE ONLY - DOES NOT PRINT
EXHAUST AIR TRAVERSE TEST REPORT
PROJECT |  |  |  | EHC - Tallahassee Reno. & Add. | [15 empty] | SYSTEM |  |  | EF-PW-04
PROJECT TOLERANCES
AREA SERVED |  |  |  | Patient Toilets | [15 empty] | LOCATION |  |  | Roof | [6 empty] | ABOVE DESIGN
BELOW DESIGN
TRAVERSE DATA
TRAVERSE AREA | [9 empty] | DESIGN AIRFLOW | [9 empty] | ACTUAL AIRFLOW | [8 empty] | FINAL CFM TOLERANCE CHECK
SIZE |  | "W |  |  | "H |  | SQ. FT. |  |  | FPM |  |  |  | CFM | [5 empty] | FPM |  |  |  |  | CFM
[12 empty] | OP. FREQ. FINAL SETTING | [7 empty] | TESTING EQUIPMENT
[20 empty] | INSTRUMENT |  |  | Air Data Multimeter - Velocity Grid
AIR VELOCITY READINGS (FPM) | [28 empty] | (W) WIDTH DISTANCE AND NO. OF POINT CALCS.
POSITION (IN.) |  |  |  |  | 1 | 2 |  | 3 | 4 |  | 5 |  | 6 | 7 |  | 8 |  | 9 |  |  | 10 | 11 |  | 12 |  | 13 | 14
NO. |  |  | POINT |  | 6 | [23 empty] | WIDTH "
1 |  |  | 6 | [25 empty] | NO. OF POINTS
2 | [28 empty] | POINT DISTANCE " | [5 empty] | GENERAL FIELD CALC. AREA
3
4 | [28 empty] | (H) HEIGHT DISTANCE AND NO. OF POINT CALCS.
5
6 | [28 empty] | HEIGHT "
7 | [28 empty] | NO. OF POINTS
8 | [28 empty] | POINT DISTANCE "
9
10 | [28 empty] | DECIMAL TO FRACTION CONVERTER (Fraction as Quarters)
SUB-TOTAL |  |  |  |  | 0 | [23 empty] | POSITION |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
[29 empty] | NO. |  | POINT | 6
| REMARKS | [17 empty] | CENTERLINE TRAVERSE SP | [7 empty] | "w.c. |  | 1 |  | 6
[19 empty] | AIR TEMPERATURE | [7 empty] | °F |  | 2
[19 empty] | TOTAL READINGS | [7 empty] | FPM |  | 3
[19 empty] | NO. READINGS | [9 empty] | 4
[19 empty] | AVG. VELOCITY | [7 empty] | FPM |  | 5
[19 empty] | EFFECTIVE AREA MULTIPLIER | [9 empty] | 6
[19 empty] | AREA | [7 empty] | SQ. FT. |  | 7
[19 empty] | TOTAL AIRFLOW | [7 empty] | CFM |  | 8
9
TEST DATE | [16 empty] | READINGS BY | [11 empty] | 10

## EF-PW-04 - EXHTRAV-PTO
INTERNAL USE ONLY - DOES NOT PRINT
EXHAUST AIR TRAVERSE TEST REPORT
PROJECT |  |  |  | EHC - Tallahassee Reno. & Add. | [16 empty] | SYSTEM |  |  | EF-PW-04
[33 empty] | PROJECT TOLERANCES | DECIMAL TO FRACTION CONVERTER (Fraction as Quarters)
AREA SERVED |  |  |  | Patient Toilets | [16 empty] | LOCATION |  |  | Roof | [8 empty] | ABOVE DESIGN | POSITION (IN.) |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
[33 empty] | BELOW DESIGN | NO. | POINT
TRAVERSE DATA | [33 empty] | 1
DUCT SIZE | [9 empty] | DESIGN AIRFLOW | [10 empty] | ACTUAL AIRFLOW | [10 empty] | FINAL CFM TOLERANCE CHECK |  | 2
"W |  |  | PORT # |  |  |  | SQ. FT. |  |  | FPM |  |  |  | CFM | [6 empty] | FPM |  |  |  |  | CFM | [7 empty] | 3
"H |  |  | PORT # | [30 empty] | 4
[8 empty] | OP. FREQ. FINAL SETTING | [6 empty] | TESTING EQUIPMENT INSTRUMENT | [8 empty] | Air Data Multimeter - Pitot Tube | [7 empty] | (W) WIDTH DISTANCE AND NO. OF POINT CALCS. |  | 5
6
AIR VELOCITY READINGS (FPM) | [31 empty] | WIDTH " |  | 7
POSITION (IN.) | [31 empty] | NO. OF POINTS |  | 8
NO. |  | POINT | VP |  | VEL | VP | VEL | VP | VEL | VP | VEL | VP | VEL | VP |  | VEL | VP |  | VEL |  | VP | VEL | VP |  | VEL | VP | VEL | VP |  | VEL |  | POINT DISTANCE " |  | 9
1 | [33 empty] | 10
2 | [31 empty] | (H) HEIGHT DISTANCE AND NO. OF POINT CALCS.
3
4 | [31 empty] | HEIGHT "
5 | [31 empty] | NO. OF POINTS
6 | [31 empty] | POINT DISTANCE "
7
8 | [31 empty] | GENERAL FIELD CALC. AREA
9
10
SUB-TOTAL
REMARKS
[20 empty] | CENTERLINE TRAVERSE ("w.c.) | [6 empty] | TP |  | SP
[20 empty] | AIR TEMPERATURE | [8 empty] | °F
[20 empty] | TOTAL READINGS | [8 empty] | FPM |  |  | If you have a VP that is 0.00 you need to unlock the sheet and adjust ALL VP
NO. READINGS
[20 empty] | AVG. VELOCITY | [8 empty] | FPM |  |  | columns to the thousandth decimal place and re-enter the traverse with three digits.
EFFECTIVE AREA MULTIPLIER
[20 empty] | AREA | [8 empty] | SQ. FT. |  |  | In most cases a 0.00 will move to a 0.002 or a 0.001 etc. A legitimate zero VP (0.00 or 0.000) is a
[20 empty] | TOTAL AIRFLOW | [8 empty] | CFM |  |  | red flag in report reviews. Note: Do not adjust the decimal place for the "VEL" columns.
TEST DATE | [17 empty] | READINGS BY

## EF-PW-04 - EXHTRAV-RNDPTO
INTERNAL USE ONLY - DOES NOT PRINT
EXHAUST AIR TRAVERSE TEST REPORT
PROJECT |  |  |  | EHC - Tallahassee Reno. & Add. | [12 empty] | SYSTEM | EF-PW-04
PROJECT TOLERANCES
AREA SERVED |  |  |  | Patient Toilets | [12 empty] | LOCATION | Roof | [5 empty] | ABOVE DESIGN
BELOW DESIGN
TRAVERSE DATA
TRAVERSE AREA | [10 empty] | DESIGN AIRFLOW | [5 empty] | ACTUAL AIRFLOW | [5 empty] | FINAL CFM TOLERANCE CHECK
SIZE |  |  | " ROUND |  |  | SQ. FT. |  | 0 |  |  | FPM |  | CFM |  |  |  | FPM |  | CFM
AIR VELOCITY READINGS (FPM) | [11 empty] | OP. FREQ. FINAL SETTING |  |  |  |  | TESTING EQUIPMENT | [5 empty] | GENERAL FIELD CALC. AREA
POSITION |  |  |  |  | X AXIS |  |  |  | Y AXIS | [7 empty] | INSTRUMENT | Air Data Multimeter - Pitot Tube
NO. |  | POINT |  |  | VP |  | VEL |  | VP | VEL
1 |  | 0
2 |  | 0
3 |  | 0
4 |  | 0
5 |  | 0
6 |  | 0
7 |  | 0
8 |  | 0
9 |  | 0
10 |  | 0
SUB-TOTAL |  |  |  |  | --- |  |  |  | ---
| REMARKS | [14 empty] | CENTERLINE TRAVERSE SP |  |  |  |  | "w.c. |  | If you have a VP that is 0.00 you need to unlock the sheet and adjust ALL VP
[16 empty] | AIR TEMPERATURE |  |  |  |  | °F
[16 empty] | TOTAL READINGS |  |  |  | 0 | FPM |  | columns to the thousandth decimal place and re-enter the traverse with three digits.
[16 empty] | NO. READINGS |  |  |  | 0
[16 empty] | AVG. VELOCITY |  |  |  |  | FPM |  | In most cases a 0.00 will move to a 0.002 or a 0.001 etc. A legitimate zero VP (0.00 or 0.000) is a
[16 empty] | EFFECTIVE AREA MULTIPLIER | [6 empty] | red flag in report reviews. Note: Do not adjust the decimal place for the "VEL" columns.
[16 empty] | AREA |  |  |  | 0 | SQ. FT.
[16 empty] | TOTAL AIRFLOW |  |  |  |  | CFM
TEST DATE | [14 empty] | READINGS BY
X AXIS
Y AXIS