## AHUFLYER
Air Handling Unit Systems Test Reports

## ahu1
INTERNAL USE ONLY - DOES NOT PRINT
SUPPLY MOTOR ACTUAL BHP CALCS.
[27 empty] | AMPS. |  | VOLTS |  |  |  | AMP IMBALANCE TEST1 | VOLT IMBALANCE TEST2
[25 empty] | TEST 1 |  |  |  |  | MOTOR EFF.
TEST 2
PROJECT | [12 empty] | SYSTEM |  |  | ahu1 | [8 empty] | TEST 3 |  |  |  |  | POWER FACTOR
[25 empty] | AVG. | [7 empty] | 1. Amp imbalance may indicate problems with the motor or power supply.
AREA SERVED |  |  | area1 | [9 empty] | LOCATION |  |  | loc1 | [13 empty] | MOTOR PHASE |  |  | 2. Volt imbalance may cause motors to overheat. Many solid-state motor controllers and inverters are sensitive to imbalanced voltage.
UNIT DATA | [12 empty] | FILTER DATA
MFG. |  |  |  | mfg1 | [8 empty] | FILTER SECTION | [11 empty] | RETURN MOTOR ACTUAL BHP CALCS.
TYPE |  |  |  | HDT | [8 empty] | QUANTITY | [13 empty] | AMPS. |  | VOLTS |  |  |  | AMP IMBALANCE TEST1 | VOLT IMBALANCE TEST2
MODEL NO. |  |  |  | no1 | [8 empty] | SIZE (in.) | [11 empty] | TEST 1 |  |  |  |  | MOTOR EFF.
SERVICE | [12 empty] | TYPE | [11 empty] | TEST 2
SERIAL NO. | [12 empty] | S.P. ACROSS | [5 empty] | "w.c. |  |  |  | "w.c. |  | TEST 3 |  |  |  |  | POWER FACTOR
[13 empty] | CONDITION | [11 empty] | AVG. | [7 empty] | 1. Amp imbalance may indicate problems with the motor or power supply.
[30 empty] | MOTOR PHASE |  |  | 2. Volt imbalance may cause motors to overheat. Many solid-state motor controllers and inverters are sensitive to imbalanced voltage.
SUPPLY FAN DATA | [8 empty] | AIRFLOW DATA | [8 empty] | RETURN FAN DATA
|  | DESIGN |  | ACTUAL | [6 empty] | DESIGN |  | ACTUAL | [6 empty] | DESIGN |  | ACTUAL
CFM |  | 100 | [6 empty] | SUPPLY |  |  |  | 0 |  |  |  |  | CFM |  | 1000 |  |  |  |  | SUPPLY POWER TRANSMISSION (PT) CALCS. | [6 empty] | RETURN POWER TRANSMISSION (PT) CALCS.
TSP |  | 1 | [6 empty] | RETURN |  | 1 |  | 0 |  |  |  |  | TSP |  | 10 |  |  |  |  | MTR TO FAN SHEAVE RATIO | [6 empty] | MTR TO FAN SHEAVE RATIO
ESP |  | 1 | [6 empty] | OUTSIDE |  | 1 |  | 0 |  |  |  |  | ESP |  | 10 |  |  |  |  | CALC. BELT LENGTH | [5 empty] | " | CALC. BELT LENGTH |  |  | "
RPM |  | 1 | [6 empty] | RELIEF | [8 empty] | RPM |  | 10 |  |  |  |  | FAN MOTOR RPM PER PT | [6 empty] | FAN MOTOR RPM PER PT
BHP |  | 1 | [15 empty] | BHP |  | 10 |  |  |  |  | MIN. FAN MTR RPM PER PT1 | [6 empty] | MIN. FAN MTR RPM PER PT1
ROTATION | [8 empty] | DUCT DIFF. PRESSURE | [8 empty] | ROTATION | [6 empty] | 1. If fan motor RPM falls below this min. number (cell red) check for belt slippage or belt riding on motor shaft. Based on 0.5" reduction on motor and fan sheave. | [6 empty] | 1. If fan motor RPM falls below this min. number (cell red) check for belt slippage or belt riding on motor shaft. Based on 0.5" reduction on motor and fan sheave.
[9 empty] | SETPOINT |  |  |  |  | "w.c.
SUPPLY FAN SPEED FINAL SETTING | [8 empty] | DDC READOUT |  |  |  |  | "w.c. | RETURN FAN SPEED FINAL SETTING
ECM SETTING | [8 empty] | ACTUAL |  |  |  |  | "w.c. | VFD SETTING | [9 empty] | DUCT DP SETPOINT CALC. (+20% Tol.)
MOTOR DATA |  |  | X | [8 empty] | MOTOR DATA |  |  | X
MFG. | [11 empty] | MFG.
FRAME | [11 empty] | FRAME
H.P. | [11 empty] | H.P.
SERVICE FACTOR | [11 empty] | SERVICE FACTOR | [12 empty] | BASIC TESTING WORKFLOW (Indicate Complete with x)
[5 empty] | DESIGN |  |  | ACTUAL | [8 empty] | DESIGN |  |  |  | ACTUAL |  |  |  |  | 1 |  | Verify duct layout (areas served) vs drawings and neck sizes.
RPM | [11 empty] | RPM | [13 empty] | 2 |  | Check nameplate against submittal.
FULL LOAD AMPS. | [7 empty] | --- |  |  |  | FULL LOAD AMPS. | [8 empty] | --- |  |  |  |  | 3 |  | Open dampers and check that automatic dampers open when the system is energized.
CRT. NAME AMPS. |  |  |  |  | --- | [6 empty] | CRT. NAME AMPS. |  |  |  |  | --- | [8 empty] | 4 |  | Check pulley alignment and tightness.
OP. AMPS. |  |  |  |  | --- | [6 empty] | OP. AMPS. |  |  |  |  | --- | [8 empty] | 5 |  | Put the unit into full cooling.
VOLTS | [11 empty] | VOLTS | [13 empty] | 6 |  | Check rotation.
[26 empty] | 7 |  | Measure the inlets / outlets on the system.
POWER TRANSMISSION DATA | [5 empty] | X | [5 empty] | POWER TRANSMISSION DATA | [6 empty] | X | [6 empty] | 8 |  | Proportion the inlets / outlets to the available airflow.
TRANSMISSION TYPE | [11 empty] | TRANSMISSION TYPE | [13 empty] | 9 |  | Adjust rpm as needed to achieve design airflow based on rpm vs cfm equation.
MOTOR SHEAVE MFG. | [11 empty] | MOTOR SHEAVE MFG. | [13 empty] | 10 |  | Adjust outside and return air to design.
MOTOR SHEAVE | [5 empty] | "I.D. |  |  |  | "O.D. |  | MOTOR SHEAVE | [6 empty] | "I.D. |  |  |  | "O.D. |  |  | 11 |  | Measure rpm, amperage and voltage.
FAN SHEAVE MFG. | [11 empty] | FAN SHEAVE MFG. | [13 empty] | 12 |  | Measure inlets / outlets on the system.
FAN SHEAVE | [5 empty] | "I.D. |  |  |  | "O.D. |  | FAN SHEAVE | [6 empty] | "I.D. |  |  |  | "O.D. |  |  | 13 |  | Record unit pressure profile (before filter, after filter, suction and discharge pressures etc.)
BELT MFG. | [11 empty] | BELT MFG. | [13 empty] | 14 |  | Measure the entering and leaving chilled water pressure and set to design if applicable.
NO. BELTS & SIZE | [6 empty] | @ |  |  |  |  | NO. BELTS & SIZE | [7 empty] | @ | [5 empty] | 15 |  | Measure the entering and leaving dry and wet bulb temperatures across the cooling coil.
CENTER DISTANCE | [7 empty] | "C.C. |  |  |  | CENTER DISTANCE | [8 empty] | "C.C. |  |  |  |  | 16 |  | Put the unit into full heating if applicable.
[26 empty] | 17 |  | Measure the total airflow and record differences to design.
| REMARKS | [24 empty] | 18 |  | Measure electric heating components or heating hot water pressures and set to design.
[26 empty] | 19 |  | Measure entering and leaving air temperature (dry bulb only).
[26 empty] | 20 |  | Make sure all information on the data sheet is filled out.
Note - Measure total supply, return and outside airflows by traverse when possible.
TEST DATE | [10 empty] | READINGS BY

## ahu1 - STATIC PRESSURE PROFILE
INTERNAL USE ONLY - DOES NOT PRINT
RETURN STATIC PRESSURE PROFILE "w.c. |  | RETURN FAN STATIC PRESSURE PROFILE |  |  | SUPPLY STATIC PRESSURE PROFILE SELECTIONS | SINGLE OR DUAL PRESSURE PROFILE?
[5 empty] | A - B | Dual
SUPPLY STATIC PRESSURE PROFILE "w.c. |  |  |  |  | B - C
COMPONENT |  |  |  |  | C - D
D - E
E - F
F - G
PRESSURE |  |  |  |  | G - H
H - I
EXHAUST STATIC PRESSURE PROFILE "w.c. |  |  |  |  | I - J
COMPONENT |  |  |  |  | J - K
EXHAUST STATIC PRESSURE PROFILE SELECTIONS
A - B
PRESSURE |  |  |  |  | B - C
C - D
| REMARKS |  |  |  | D - E
E - F
F - G
G - H
H - I
I - J
J - K
TEST DATE |  |  | READINGS BY

## ahu1 - SPLYCURVE
ahu1 - SUPPLY FAN CURVE PLACEHOLDER

## ahu1 - SUPTRAV-PTO
INTERNAL USE ONLY - DOES NOT PRINT
SUPPLY AIR TRAVERSE REPORT
PROJECT | [21 empty] | SYSTEM |  |  | ahu1
[34 empty] | PROJECT TOLERANCES | DECIMAL TO FRACTION CONVERTER (Fraction as Quarters)
AREA SERVED |  |  |  | area1 | [17 empty] | LOCATION |  |  | loc1 | [8 empty] | ABOVE DESIGN | POSITION (IN.) |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
[34 empty] | BELOW DESIGN | NO. | POINT
TRAVERSE DATA | [34 empty] | 1
DUCT SIZE | [9 empty] | DESIGN AIRFLOW | [11 empty] | ACTUAL AIRFLOW | [10 empty] | FINAL CFM TOLERANCE CHECK |  | 2
"W |  |  | PORT # |  |  |  | SQ. FT. |  |  | FPM |  |  |  | CFM |  |  | 100 |  |  |  |  | FPM |  |  |  |  | CFM | [7 empty] | 3
"H |  |  | PORT # | [31 empty] | 4
[8 empty] | OP. FREQ. FINAL SETTING | [6 empty] | TESTING EQUIPMENT INSTRUMENT | [9 empty] | Air Data Multimeter - Pitot Tube | [7 empty] | (W) WIDTH DISTANCE AND NO. OF POINT CALCS. |  | 5
6
AIR VELOCITY READINGS (FPM) | [32 empty] | WIDTH " |  | 7
POSITION (IN.) | [32 empty] | NO. OF POINTS |  | 8
NO. |  | POINT | VP |  | VEL | VP | VEL | VP | VEL | VP | VEL | VP | VEL | VP |  | VEL |  | VP |  | VEL |  | VP | VEL | VP |  | VEL | VP | VEL | VP |  | VEL |  | POINT DISTANCE " |  | 9
1 | [34 empty] | 10
2 | [32 empty] | (H) HEIGHT DISTANCE AND NO. OF POINT CALCS.
3
4 | [32 empty] | HEIGHT "
5 | [32 empty] | NO. OF POINTS
6 | [32 empty] | POINT DISTANCE "
7
8 | [32 empty] | GENERAL FIELD CALC. AREA
9
10
SUB-TOTAL
REMARKS
[21 empty] | CENTERLINE TRAVERSE ("w.c.) | [6 empty] | TP |  | SP
[21 empty] | AIR TEMPERATURE | [8 empty] | °F
[21 empty] | TOTAL READINGS | [8 empty] | FPM |  |  | If you have a VP that is 0.00 you need to unlock the sheet and adjust ALL VP
NO. READINGS
[21 empty] | AVG. VELOCITY | [8 empty] | FPM |  |  | columns to the thousandth decimal place and re-enter the traverse with three digits.
EFFECTIVE AREA MULTIPLIER
[21 empty] | AREA | [8 empty] | SQ. FT. |  |  | In most cases a 0.00 will move to a 0.002 or a 0.001 etc. A legitimate zero VP (0.00 or 0.000) is a
[21 empty] | TOTAL AIRFLOW | [8 empty] | CFM |  |  | red flag in report reviews. Note: Do not adjust the decimal place for the "VEL" columns.
TEST DATE | [18 empty] | READINGS BY

## ahu1 - RTNTRAV-VEL
INTERNAL USE ONLY - DOES NOT PRINT
RETURN AIR TRAVERSE REPORT
PROJECT | [19 empty] | SYSTEM |  |  | ahu1
PROJECT TOLERANCES
AREA SERVED |  |  |  | area1 | [15 empty] | LOCATION |  |  | loc1 | [6 empty] | ABOVE DESIGN
BELOW DESIGN
TRAVERSE DATA
TRAVERSE AREA | [9 empty] | DESIGN AIRFLOW | [9 empty] | ACTUAL AIRFLOW | [8 empty] | FINAL CFM TOLERANCE CHECK
SIZE |  | "W |  |  | "H |  | SQ. FT. |  |  | FPM |  |  |  | CFM |  | 1000 |  |  |  | FPM |  |  |  |  | CFM
[12 empty] | OP. FREQ. FINAL SETTING | [7 empty] | TESTING EQUIPMENT
[20 empty] | INSTRUMENT |  |  | Air Data Multimeter - Velocity Grid
AIR VELOCITY READINGS (FPM) | [28 empty] | (W) WIDTH DISTANCE AND NO. OF POINT CALCS.
POSITION (IN.) |  |  |  |  | 1 | 2 |  | 3 | 4 |  | 5 |  | 6 | 7 |  | 8 |  | 9 |  |  | 10 | 11 |  | 12 |  | 13 | 14
NO. |  |  | POINT |  | 6 | [23 empty] | WIDTH "
1 |  |  | 6 | [25 empty] | NO. OF POINTS
2 | [28 empty] | POINT DISTANCE " | [5 empty] | GENERAL FIELD CALC. AREA
3
4 | [28 empty] | (H) HEIGHT DISTANCE AND NO. OF POINT CALCS.
5
6 | [28 empty] | HEIGHT "
7 | [28 empty] | NO. OF POINTS
8 | [28 empty] | POINT DISTANCE "
9
10 | [28 empty] | DECIMAL TO FRACTION CONVERTER (Fraction as Quarters)
SUB-TOTAL |  |  |  |  | 0 | [23 empty] | POSITION |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
[29 empty] | NO. |  | POINT | 6
| REMARKS | [17 empty] | CENTERLINE TRAVERSE SP | [7 empty] | "w.c. |  | 1 |  | 6
[19 empty] | AIR TEMPERATURE | [7 empty] | °F |  | 2
[19 empty] | TOTAL READINGS | [7 empty] | FPM |  | 3
[19 empty] | NO. READINGS | [9 empty] | 4
[19 empty] | AVG. VELOCITY | [7 empty] | FPM |  | 5
[19 empty] | EFFECTIVE AREA MULTIPLIER | [9 empty] | 6
[19 empty] | AREA | [7 empty] | SQ. FT. |  | 7
[19 empty] | TOTAL AIRFLOW | [7 empty] | CFM |  | 8
9
TEST DATE | [16 empty] | READINGS BY | [11 empty] | 10

## ahu1 - RTNTRAV-PTO
INTERNAL USE ONLY - DOES NOT PRINT
RETURN AIR TRAVERSE REPORT
PROJECT | [21 empty] | SYSTEM |  |  | ahu1
[34 empty] | PROJECT TOLERANCES | DECIMAL TO FRACTION CONVERTER (Fraction as Quarters)
AREA SERVED |  |  |  | area1 | [17 empty] | LOCATION |  |  | loc1 | [8 empty] | ABOVE DESIGN | POSITION (IN.) |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
[34 empty] | BELOW DESIGN | NO. | POINT
TRAVERSE DATA | [34 empty] | 1
DUCT SIZE | [9 empty] | DESIGN AIRFLOW | [11 empty] | ACTUAL AIRFLOW | [10 empty] | FINAL CFM TOLERANCE CHECK |  | 2
"W |  |  | PORT # |  |  |  | SQ. FT. |  |  | FPM |  |  |  | CFM |  |  | 1000 |  |  |  |  | FPM |  |  |  |  | CFM | [7 empty] | 3
"H |  |  | PORT # | [31 empty] | 4
[8 empty] | OP. FREQ. FINAL SETTING | [6 empty] | TESTING EQUIPMENT INSTRUMENT | [9 empty] | Air Data Multimeter - Pitot Tube | [7 empty] | (W) WIDTH DISTANCE AND NO. OF POINT CALCS. |  | 5
6
AIR VELOCITY READINGS (FPM) | [32 empty] | WIDTH " |  | 7
POSITION (IN.) | [32 empty] | NO. OF POINTS |  | 8
NO. |  | POINT | VP |  | VEL | VP | VEL | VP | VEL | VP | VEL | VP | VEL | VP |  | VEL |  | VP |  | VEL |  | VP | VEL | VP |  | VEL | VP | VEL | VP |  | VEL |  | POINT DISTANCE " |  | 9
1 | [34 empty] | 10
2 | [32 empty] | (H) HEIGHT DISTANCE AND NO. OF POINT CALCS.
3
4 | [32 empty] | HEIGHT "
5 | [32 empty] | NO. OF POINTS
6 | [32 empty] | POINT DISTANCE "
7
8 | [32 empty] | GENERAL FIELD CALC. AREA
9
10
SUB-TOTAL
REMARKS
[21 empty] | CENTERLINE TRAVERSE ("w.c.) | [6 empty] | TP |  | SP
[21 empty] | AIR TEMPERATURE | [8 empty] | °F
[21 empty] | TOTAL READINGS | [8 empty] | FPM |  |  | If you have a VP that is 0.00 you need to unlock the sheet and adjust ALL VP
NO. READINGS
[21 empty] | AVG. VELOCITY | [8 empty] | FPM |  |  | columns to the thousandth decimal place and re-enter the traverse with three digits.
EFFECTIVE AREA MULTIPLIER
[21 empty] | AREA | [8 empty] | SQ. FT. |  |  | In most cases a 0.00 will move to a 0.002 or a 0.001 etc. A legitimate zero VP (0.00 or 0.000) is a
[21 empty] | TOTAL AIRFLOW | [8 empty] | CFM |  |  | red flag in report reviews. Note: Do not adjust the decimal place for the "VEL" columns.
TEST DATE | [18 empty] | READINGS BY

## ahu1 - RTNTRAV-RNDPTO
INTERNAL USE ONLY - DOES NOT PRINT
RETURN AIR TRAVERSE REPORT
PROJECT | [17 empty] | SYSTEM | ahu1
PROJECT TOLERANCES
AREA SERVED |  |  |  | area1 | [13 empty] | LOCATION | loc1 | [5 empty] | ABOVE DESIGN
BELOW DESIGN
TRAVERSE DATA
TRAVERSE AREA | [10 empty] | DESIGN AIRFLOW | [6 empty] | ACTUAL AIRFLOW | [5 empty] | FINAL CFM TOLERANCE CHECK
SIZE |  |  | " ROUND |  |  | SQ. FT. |  | 0 |  |  | FPM |  | CFM |  | 1000 |  |  | FPM |  | CFM
AIR VELOCITY READINGS (FPM) | [11 empty] | OP. FREQ. FINAL SETTING | [5 empty] | TESTING EQUIPMENT | [5 empty] | GENERAL FIELD CALC. AREA
POSITION |  |  |  |  | X AXIS |  |  |  | Y AXIS | [8 empty] | INSTRUMENT | Air Data Multimeter - Pitot Tube
NO. |  | POINT |  |  | VP |  | VEL |  | VP | VEL
1 |  | 0
2 |  | 0
3 |  | 0
4 |  | 0
5 |  | 0
6 |  | 0
7 |  | 0
8 |  | 0
9 |  | 0
10 |  | 0
SUB-TOTAL |  |  |  |  | --- |  |  |  | ---
| REMARKS | [15 empty] | CENTERLINE TRAVERSE SP |  |  |  |  | "w.c. |  | If you have a VP that is 0.00 you need to unlock the sheet and adjust ALL VP
[17 empty] | AIR TEMPERATURE |  |  |  |  | °F
[17 empty] | TOTAL READINGS |  |  |  | 0 | FPM |  | columns to the thousandth decimal place and re-enter the traverse with three digits.
[17 empty] | NO. READINGS |  |  |  | 0
[17 empty] | AVG. VELOCITY |  |  |  |  | FPM |  | In most cases a 0.00 will move to a 0.002 or a 0.001 etc. A legitimate zero VP (0.00 or 0.000) is a
[17 empty] | EFFECTIVE AREA MULTIPLIER | [6 empty] | red flag in report reviews. Note: Do not adjust the decimal place for the "VEL" columns.
[17 empty] | AREA |  |  |  | 0 | SQ. FT.
[17 empty] | TOTAL AIRFLOW |  |  |  |  | CFM
TEST DATE | [15 empty] | READINGS BY
X AXIS
Y AXIS

## ahu1 - OUTLETSUM-1
INTERNAL USE ONLY - DOES NOT PRINT
OUTLET TEST REPORT
PROJECT | [6 empty] | SYSTEM |  | ahu1
PROJECT TOLERANCES
[16 empty] | ABOVE DESIGN | GENERAL FIELD CALC. AREA
[14 empty] | FOR PROPORTIONS, CORRECTION FACTORS, ETC. |  | BELOW DESIGN
AREA SERVED LOCATION |  | OUTLETS |  |  |  | DESIGN CFM | PRELIMINARY CFM |  |  |  | FINAL CFM | REMARKS
|  | NO. | TYPE |  | SIZE (IN.) |  | TEST1 | TEST 2 |  | TEST 3 |  |  |  |  | FINAL CFM TOLERANCE CHECK
TOTAL
REMARKS
TEST DATE | [5 empty] | READINGS BY

## ahu1 - ATUSUM
INTERNAL USE ONLY - DOES NOT PRINT
AIR TERMINAL UNIT SUMMARY REPORT
PROJECT | [10 empty] | SYSTEM |  | ahu1
AIR TERMINAL UNIT DATA | [16 empty] | GENERAL FIELD CALC. AREA
AIR TERMINAL NO. |  | AIRFLOW |  |  |  | FAN |  | HEATING |  | CALIBRATION DATA |  |  |  |  | REMARKS
|  | DESIGN MAX. | ACTUAL MAX. | DESIGN MIN. | ACTUAL MIN. | DESIGN FAN | ACTUAL FAN | DESIGN HEAT MAX | ACTUAL HEAT MAX | CALIBRATION CODE |  | INLET SIZE (IN.) |  | DDC. ADDRESS
key1 |  | 0 |  | 0 | 0 | --- | --- | 0 | 0 | 0 |  | 0 |  | 0
key2 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0
key3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
TOTAL |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REMARKS

## key1
INTERNAL USE ONLY - DOES NOT PRINT
VARIABLE AIR VOLUME UNIT TEST REPORT
PROJECT | [7 empty] | SYSTEM |  | ahu1 | [5 empty] | BASIC TESTING WORKFLOW (Indicate Complete with x) | [5 empty] | TIME TO COMPLETE STEPS (MINS.)
[22 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42
AREA SERVED | [7 empty] | LOCATION | [8 empty] | 1 | Get controls communicating. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
[17 empty] | 2 | Verify duct layout vs drawings with neck size. | bar: TIME TO COMPLETE STEPS (MINS.) 1 to TIME TO COMPLETE STEPS (MINS.) 5
VAV UNIT DATA | [7 empty] | VAV PERFORMANCE DATA | [8 empty] | 3 | Open dampers. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 10
VAV # | key1 | [9 empty] | DESIGN |  | ACTUAL |  |  |  | 4 | Put box in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 6 to TIME TO COMPLETE STEPS (MINS.) 7
INLET SIZE |  |  |  | " |  |  |  | CLG. MAX. CFM | [8 empty] | 5 | Nameplate check against submittal. | bar: TIME TO COMPLETE STEPS (MINS.) 8 to TIME TO COMPLETE STEPS (MINS.) 10
MFG. | [7 empty] | CLG. MIN. CFM | [8 empty] | 6 | Measure outlets in cooling. | bar: TIME TO COMPLETE STEPS (MINS.) 11 to TIME TO COMPLETE STEPS (MINS.) 15
TYPE | [7 empty] | HTG. MAX. CFM | [8 empty] | 7 | Calibrate flow at max. | bar: TIME TO COMPLETE STEPS (MINS.) 16 to TIME TO COMPLETE STEPS (MINS.) 17
MODEL NO. | [7 empty] | HTG. MIN. CFM | [8 empty] | 8 | Balance at calibrated max w/ double check readings. | bar: TIME TO COMPLETE STEPS (MINS.) 18 to TIME TO COMPLETE STEPS (MINS.) 27
SERVICE | Conditioned Air | [15 empty] | 9 | Put box to satisfied. | bar: TIME TO COMPLETE STEPS (MINS.) 28 to TIME TO COMPLETE STEPS (MINS.) 29
SERIAL NO. | [16 empty] | 10 | Measure outlets in satisfied condition, record flow. | bar: TIME TO COMPLETE STEPS (MINS.) 30 to TIME TO COMPLETE STEPS (MINS.) 32
DDC TERMINAL # | [16 empty] | 11 | Put box in heat. | bar: TIME TO COMPLETE STEPS (MINS.) 33 to TIME TO COMPLETE STEPS (MINS.) 34
COR. FACTOR | [16 empty] | 12 | Measure outlets and record total. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 2: LEGEND
[17 empty] | 13 | Measure elec. heat components (or water). |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: EIT
[17 empty] | 14 | Measure LAT. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TECH
[17 empty] | 15 | Release the box. |  |  |  | TIME TO COMPLETE STEPS (MINS.) 3: TEAM
[17 empty] | 16 | Make sure all information on the data sheet is filled out.
[20 empty] | PROJECT TOLERANCES | GENERAL FIELD CALC. AREA
ABOVE DESIGN
[16 empty] | FOR PROPORTIONS, CORRECTION FACTORS, ETC. |  |  |  | BELOW DESIGN
AREA SERVED LOCATION |  | OUTLETS |  |  |  |  | DESIGN CFM | PRELIMINARY CFM |  |  |  | FINAL CFM |  | REMARKS
|  | NO. | TYPE |  |  | SIZE (IN.) |  | TEST1 | TEST 2 |  | TEST 3 | [7 empty] | FINAL CFM TOLERANCE CHECK
TOTAL
REMARKS
TEST DATE | [6 empty] | READINGS BY

## key2
INTERNAL USE ONLY - DOES NOT PRINT
GENERAL FIELD CALC. AREA
SERIES FAN POWERED BOX TEST REPORT
PROJECT | [8 empty] | SYSTEM |  | ahu1
AREA SERVED | [8 empty] | LOCATION
FAN POWERED BOX DATA | [7 empty] | FAN MOTOR DATA | [8 empty] | MOTOR ACTUAL AMPS. & VOLTS CALCS.
BOX # | key2 | [10 empty] | DESIGN |  | ACTUAL |  |  |  | AMPS. | VOLTS |  |  |  | AMP IMBALANCE TEST1 |  | VOLT IMBALANCE TEST2
INLET SIZE |  |  |  | " |  |  |  | H.P. | [8 empty] | TEST 1
MFG. | [7 empty] | AMPS. | [8 empty] | TEST 2
TYPE | [7 empty] | VOLTS | [8 empty] | TEST 3
MODEL NO. | [16 empty] | AVG. | [5 empty] | 1. Amp imbalance may indicate problems with the motor or power supply.
SERVICE | Conditioned Air | [7 empty] | FAN PERFORMANCE DATA | [10 empty] | MOTOR PHASE |  |  | 2. Volt imbalance may cause motors to overheat. Many solid-state motor controllers and inverters are sensitive to imbalanced voltage.
SERIAL NO. | [11 empty] | DESIGN |  | ACTUAL
DDC TERMINAL # | [8 empty] | CLG. MAX. CFM
COR. FACTOR | [8 empty] | CLG. MIN. CFM | [14 empty] | DETERMINING FAN ROTATION
FAN CFM
HTG. MAX CFM
FINAL SETTINGS
MOTOR SPEED SETTING
PROJECT TOLERANCES
ABOVE DESIGN
[17 empty] | FOR PROPORTIONS, CORRECTION FACTORS, ETC. |  |  |  |  | BELOW DESIGN
AREA SERVED LOCATION |  | OUTLETS |  |  |  |  | DESIGN CFM |  | PRELIMINARY CFM |  |  |  | FINAL CFM |  | REMARKS
|  | NO. | TYPE |  |  | SIZE |  |  | TEST1 | TEST 2 |  | TEST 3 | [8 empty] | FINAL CFM TOLERANCE CHECK
TOTAL
REMARKS
TEST DATE | [6 empty] | READINGS BY
LOOKING
CCW

## key3
INTERNAL USE ONLY - DOES NOT PRINT
PARALLEL FAN POWERED BOX TEST REPORT
PROJECT | [8 empty] | SYSTEM |  | ahu1
AREA SERVED | [8 empty] | LOCATION
FAN POWERED BOX DATA | [7 empty] | FAN MOTOR DATA | [8 empty] | MOTOR ACTUAL AMPS. & VOLTS CALCS.
BOX # | key3 | [10 empty] | DESIGN |  | ACTUAL |  |  |  | AMPS. | VOLTS |  |  |  | AMP IMBALANCE TEST1 |  | VOLT IMBALANCE TEST2
INLET SIZE |  |  |  | " |  |  |  | H.P. | [8 empty] | TEST 1
MFG. | [7 empty] | AMPS. | [8 empty] | TEST 2
TYPE | [7 empty] | VOLTS | [8 empty] | TEST 3
MODEL NO. | [16 empty] | AVG. | [5 empty] | 1. Amp imbalance may indicate problems with the motor or power supply.
SERVICE | Conditioned Air | [7 empty] | FAN PERFORMANCE DATA | [10 empty] | MOTOR PHASE |  |  | 2. Volt imbalance may cause motors to overheat. Many solid-state motor controllers and inverters are sensitive to imbalanced voltage.
SERIAL NO. | [11 empty] | DESIGN |  | ACTUAL
DDC TERMINAL # | [8 empty] | CLG. MAX. CFM
COR. FACTOR | [8 empty] | CLG. MIN. CFM | [7 empty] | GENERAL FIELD CALC. AREA | [6 empty] | DETERMINING FAN ROTATION
FAN CFM
[9 empty] | HTG. MAX CFM |  |  |  |  | 0
FINAL SETTINGS
MOTOR SPEED SETTING
PROJECT TOLERANCES
ABOVE DESIGN
[17 empty] | FOR PROPORTIONS, CORRECTION FACTORS, ETC. |  |  |  |  | BELOW DESIGN
AREA SERVED LOCATION |  | OUTLETS |  |  |  |  | DESIGN CFM |  | PRELIMINARY CFM |  |  |  | FINAL CFM |  | REMARKS
|  | NO. | TYPE |  |  | SIZE |  |  | TEST1 | TEST 2 |  | TEST 3 | [8 empty] | FINAL CFM TOLERANCE CHECK
TOTAL
REMARKS
TEST DATE | [6 empty] | READINGS BY
LOOKING
CCW